## Info
Name | RCX
Version | 2.0-1-00
Description | RCX Room Controller 2.0-1-00

## en
RCX-2.0-1-00 ꟷ Menu Structure |  |  |  | Revision: A
Tab | Menu | Group | Item | Description
Dashboard
Overview
System
|  |  | Controller | Model number (Model)
|  |  | Version | The application version as a string (VersionNumberString)
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
|  |  | Modbus address | Active Modbus unit ID (ModbusUnitID)
|  |  | BACnet MSTP address | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | BACnet device ID | BACnet device ID (BACnetDeviceID)
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
Room
|  |  | Controller state | Current state (RC_ControllerState)
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Room temperature (°C) | Room temperature (RC_RoomTemp)
|  |  | Supply air temperature (°C) | Supply air temperature (RC_SupplyAirTemp)
|  |  | Room setpoint (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Setpoint adjustment (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | EC fan speed (%) | Current EC fan speed (RC_ECFanSpeed)
|  |  | CO2 level (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | Room humidity (%) | Relative humidity (RC_Humidity)
|  |  | VOC index | VOC index (RC_VOC)
|  |  | Presence detection | Presence indication (RC_Presence)
|  |  | Condensation | Condensation indication (RC_DICondensation)
Extra zone
|  |  | Extra zone temperature (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
|  |  | Extra zone setpoint (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
|  |  | Extra zone active output | Extra Zone active (RC_ExtraZoneActive)
Actual values
Room Control Sequence
|  |  | Sequence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Actual values
|  |  | Mode | Current controller mode (RC_ControllerMode)
|  |  | Room temperature (°C) | Room temperature (RC_RoomTemp)
|  |  | Room setpoint (°C) | Active room control setpoint (RC_RoomActiveSetpoint)
|  |  | Setpoint adjustment (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
|  |  | Heating demand (%) | Room PID heat output (RC_PIDHeatDemand)
|  |  | Cooling demand (%) | Room PID cool output (RC_PIDCoolDemand)
|  |  | Heating output (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Heating 2 output (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Cooling output (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Cooling 2 output (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | VAV output (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
|  |  | VAV 2 output (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
|  |  | Change-over temperature | Changeover temperature (RC_ChangeOverTemp)
|  |  | Change-over state | Change-over status (RC_ChangeOverState)
|  |  | Change-over output (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
|  |  | Change-over VAV temperature | Changeover VAV temperature (RC_ChangeOverVAVTemp)
|  |  | Change-over VAV state | Change-over VAV status (RC_ChangeOverStateVAV)
|  |  | Change-over VAV output (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
|  |  | 6-way valve output (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
|  |  | CO2 level (ppm) | Rounded room CO2 level (RC_CO2LevelRounded)
|  |  | CO2 setpoint (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Relay output
|  |  | Relay state | Value set for output (IoDo_3_value)
|  |  | Source 1 | First input source for the relay control function (out_relay_source_1)
|  |  | Deactivate Limit | This value on the source channel should map to 0 (out_relay_source_1_map_min)
|  |  | Activate Limit | This value on the source channel should map to 1 (out_relay_source_1_map_max)
|  |  | Source 2 | Second input source for the relay control function (out_relay_source_2)
|  |  | Deactivate Limit | This value on the source channel should map to 0 (out_relay_source_2_map_min)
|  |  | Activate Limit | This value on the source channel should map to 1 (out_relay_source_2_map_max)
|  |  | Source 3 | Third input source for the relay control function (out_relay_source_3)
|  |  | Deactivate Limit | This value on the source channel should map to 0 (out_relay_source_3_map_min)
|  |  | Activate Limit | This value on the source channel should map to 1 (out_relay_source_3_map_max)
|  |  | Source 4 | Forth input source for the relay control function (out_relay_source_4)
|  |  | Deactivate Limit | This value on the source channel should map to 0 (out_relay_source_4_map_min)
|  |  | Activate Limit | This value on the source channel should map to 1 (out_relay_source_4_map_max)
Timer
|  |  | Timer state | Current timer state (rt_exttime_state)
|  |  | Active timer value | Time remaining (rt_exttime_timeleft)
Inputs/Outputs
Universal inputs
|  |  | UI1: | Filtered value from sensor (IoAnaIn_1_value)
|  |  | UI1: | Filtered value from sensor (IoDiIn_1_value)
|  |  | UI2: | Filtered value from sensor (IoAnaIn_2_value)
|  |  | UI2: | Filtered value from sensor (IoDiIn_2_value)
|  |  | CI | Filtered value from sensor (IoDiIn_3_value)
Universal outputs
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | UO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | UO2: | Value set for output (IoDo_2_value)
Analog outputs
|  |  | AO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | AO2: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
Internal sensors
|  |  | Room temperature (°C) | Filtered value from sensor (IoAnaIn_5_value)
|  |  | CO2 sensor (ppm) | Filtered value from sensor (IoAnaIn_8_value)
|  |  | RH sensor (%) | Filtered value from sensor (IoAnaIn_6_value)
|  |  | VOC sensor | Filtered value from sensor (IoAnaIn_7_value)
|  |  | PIR sensor | Filtered value from sensor (IoDiIn_4_value)
Alarms
Alarms
|  |  | Sum alarm | Sum Alarm (RC_SumAlarm)
|  |  | Sensor error | Sensor error alarm (RC_AlarmSensorError)
|  |  | High room temperature | High room temp alarm (RC_AlarmRoomTempHigh)
|  |  | Low room temperature | Low room temp alarm (RC_AlarmRoomTempLow)
|  |  | High CO2 level | High CO2 alarm (RC_AlarmCO2High)
|  |  | External alarm (DI) | Digital input alarm (RC_AlarmDI)
|  |  | Output in manual mode | Alarm when an output is set to manual (RC_AlarmManualOutput)
|  |  | Temperature sensor error code | Detailed fault description (IoAnaIn_5_errorFlags)
|  |  | Humidity sensor error code | Detailed fault description (IoAnaIn_6_errorFlags)
|  |  | VOC sensor error code | Detailed fault description (IoAnaIn_7_errorFlags)
|  |  | CO2 sensor error code | Detailed fault description (IoAnaIn_8_errorFlags)
About
Controller ID
|  |  | Serial number | (SerialNumberString)
|  |  | Name | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Location | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Configuration
Control functions
Room Control Sequence
|  |  | Sequence 1 | Room sequence step 1 function (RC_RoomSeq1Function)
|  |  | Sequence 2 | Room sequence step 2 function (RC_RoomSeq2Function)
|  |  | Sequence 3 | Room sequence step 3 function (RC_RoomSeq3Function)
Heat
|  |  | Max limit (%) | Heat1 maximum output for all controller states. (RC_Heat1OutputMax)
|  |  | Min limit (%) | Heat1 minimum output for all controller states. (RC_Heat1OutputMin)
|  |  | Fan off delay for electric heater | Heat1 enable afterblow function (RC_Heat1Afterblow)
|  |  | Follow change-over state | Heat1 included in change-over function (RC_Heat1InChangeOver)
Heat 2
|  |  | Max limit (%) | Heat2 maximum output for all controller states. (RC_Heat2OutputMax)
|  |  | Min limit (%) | Heat2 minimum output for all controller states. (RC_Heat2OutputMin)
|  |  | Fan off delay for electric heater | Heat2 enable afterblow function (RC_Heat2Afterblow)
|  |  | Follow change-over state | Heat2 included in change-over function (RC_Heat2InChangeOver)
Cool
|  |  | Max limit (%) | Cool1 maximum output for all controller states. (RC_Cool1OutputMax)
|  |  | Min limit (%) | Cool1 minimum output for all controller states. (RC_Cool1OutputMin)
|  |  | Set to max at forced ventilation state | Set Cool1 output to max value when forced ventilation is active (RC_Cool1OutputMaxWhenForced)
|  |  | Follow change-over state | Cool1 included in change-over function (RC_Cool1InChangeOver)
Cool 2
|  |  | Max limit (%) | Cool2 maximum output for all controller states. (RC_Cool2OutputMax)
|  |  | Min limit (%) | Cool2 minimum output for all controller states. (RC_Cool2OutputMin)
|  |  | Set to max at forced ventilation state | Set Cool2 output to max value when forced ventilation is active (RC_Cool2OutputMaxWhenForced)
|  |  | Follow change-over state | Cool2 included in change-over function (RC_Cool2InChangeOver)
VAV
|  |  | Max limit (%) | VAV1 maximum output for all controller states. (RC_VAV1OutputMax)
|  |  | Min limit, off (%) | VAV1 minimum output in Off state. (RC_VAV1OutputMinOff)
|  |  | Min limit, unoccupied (%) | VAV1 minimum output in Unoccupied state. (RC_VAV1OutputMinUnoccupied)
|  |  | Min limit, standby (%) | VAV1 minimum output in Standby state. (RC_VAV1OutputMinStandby)
|  |  | Min limit, occupied (%) | VAV1 minimum output in Occupied state (RC_VAV1OutputMinOccupied)
|  |  | Min limit, forced ventilation (%) | VAV1 minimum output in Bypass state. (RC_VAV1OutputMinBypass)
|  |  | Set to max at forced ventilation state | Set VAV1 output to max value when forced ventilation is active (RC_VAV1OutputMaxWhenForced)
|  |  | Max limit when heating (%) | VAV1 maximum output when the controller is in heating mode. (RC_VAV1OutputMaxHeat)
|  |  | Follow change-over state | VAV1 included in change-over function (RC_VAV1InChangeOver)
VAV 2
|  |  | Max limit (%) | VAV2 maximum output for all controller states. (RC_VAV2OutputMax)
|  |  | Min limit, off (%) | VAV2 minimum output in Off state. (RC_VAV2OutputMinOff)
|  |  | Min limit, unoccupied (%) | VAV2 minimum output in Unoccupied state. (RC_VAV2OutputMinUnoccupied)
|  |  | Min limit, standby (%) | VAV2 minimum output in Standby state. (RC_VAV2OutputMinStandby)
|  |  | Min limit, occupied (%) | VAV2 minimum output in Occupied state (RC_VAV2OutputMinOccupied)
|  |  | Min limit, forced ventilation (%) | VAV2 minimum output in Bypass state. (RC_VAV2OutputMinBypass)
|  |  | Set to max at forced ventilation state | Set VAV2 output to max value when forced ventilation is active (RC_VAV2OutputMaxWhenForced)
|  |  | Max limit when heating (%) | VAV2 maximum output when the controller is in heating mode. (RC_VAV2OutputMaxHeat)
|  |  | Follow change-over state | VAV2 included in change-over function (RC_VAV2InChangeOver)
VAV control source
|  |  | Cooling demand | VAV is controlled by cooling output (RC_VAVControlCooling)
|  |  | CO2 level | VAV is controlled by CO2 output (RC_VAVControlCO2)
|  |  | VOC index | VAV is controlled by VOC output (RC_VAVControlVOC)
|  |  | Humidity | VAV controlled by humidify or dehumidify output (RC_VAVControlHumidity)
Change-over
|  |  | Max limit (%) | Changeover maximum output for all controller states. (RC_ChangeOverOutputMax)
|  |  | Min limit (%) | Changeover minimum output for all controller states. (RC_ChangeOverOutputMin)
|  |  | Mode | Type of detection to control change-over. (RC_ChangeOverSelect)
|  |  | Change-over temperature (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverTemperature)
|  |  | Heating hysteresis (°C) | Offset subtracted from the reference temperature when heating. (RC_ChangeOverTempHystHeat)
|  |  | Cooling hysteresis (°C) | Offset added to the reference temperature when cooling. (RC_ChangeOverTempHystCool)
|  |  | Valve delay time (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverValveTime)
Change-over VAV
|  |  | Max limit (%) | ChangeOverVAV maximum output for all controller states. (RC_ChangeOverVAVOutputMax)
|  |  | Min limit, off (%) | ChangeOverVAV minimum output in Off state. (RC_ChangeOverVAVOutputMinOff)
|  |  | Min limit, unoccupied (%) | ChangeOverVAV minimum output in Unoccupied state. (RC_ChangeOverVAVOutputMinUnoccupied)
|  |  | Min limit, standby (%) | ChangeOverVAV minimum output in Standby state. (RC_ChangeOverVAVOutputMinStandby)
|  |  | Min limit, occupied (%) | ChangeOverVAV minimum output in Occupied state (RC_ChangeOverVAVOutputMinOccupied)
|  |  | Min limit, forced ventilation (%) | ChangeOverVAV minimum output in Bypass state. (RC_ChangeOverVAVOutputMinBypass)
|  |  | Set to max at forced ventilation state | Set ChangeOverVAV output to max value when forced ventilation is active (RC_ChangeOverVAVOutputMaxWhenForced)
|  |  | Mode | Type of detection to control change-over VAV. (RC_ChangeOverVAVSelect)
|  |  | Change-over temperature (°C) | The reference temperature to use in simple mode, in advanced mode the room temperature is used (RC_ChangeOverVAVTemperature)
|  |  | Heating hysteresis (°C) | Offset added to the reference temperature when switching to heat mode. (RC_ChangeOverVAVTempHystHeat)
|  |  | Cooling hysteresis (°C) | Offset subtracted from the reference temperature when switching to cool mode. (RC_ChangeOverVAVTempHystCool)
|  |  | Valve delay time (s) | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. (RC_ChangeOverVAVValveTime)
6-way valve
|  |  | Seq 1 fully open (V) | Voltage applied to 6 way valve for fully open at sequence 1 (RC_SixWayValveFirstSeqFullyOpen)
|  |  | Seq 1 start opening (V) | Voltage applied to 6 way valve to start open at sequence 1 (RC_SixWayValveFirstSeqStartOpen)
|  |  | Seq 2 fully open (V) | Voltage applied to 6 way valve for fully open at sequence 2 (RC_SixWayValveSecondSeqFullyOpen)
|  |  | Seq 2 start opening (V) | Voltage applied to 6 way valve to start open at sequence 2 (RC_SixWayValveSecondSeqStartOpen)
|  |  | Center point (V) | Voltage applied to 6 way valve for center point, closed both sequences (RC_SixWayValveCenterPoint)
|  |  | Center point hysteresis (%) | Center point Hysteresis (RC_SixWayValveCenterPointHyst)
|  |  | Sequence order | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence (RC_SixWayValveSequenceOrder)
|  |  | Follow change-over state | 6 way valve included in change-over function (RC_SixWayValveInChangeOver)
Controller state
|  |  | Preset state | The default state when nothing else is controlling the state. (RC_ControllerStateDefault)
|  |  | Shutdown state | The state to enter when shutdown mode is set. (RC_ControllerStateShutdown)
|  |  | Window open state | The state to enter when the window is opened (RC_ControllerStateWindow)
|  |  | Time in forced ventilation state (min) | Bypass time (minutes) (RC_BypassTime)
Forced ventilation
|  |  | Active when | Forced ventilation function (RC_ForcedVentMode)
|  |  | Start limit (%) | Forced ventilation start limit (RC_ForcedVentStartLimit)
Presence detection
|  |  | Presence state | The state to enter when presence is detected. (RC_ControllerStatePresence)
|  |  | Active delay (min) | Delay for presence on (min) (RC_PresenceDelayOn)
|  |  | Inactive delay (min) | Delay for presence off (min) (RC_PresenceDelayOff)
|  |  | CO2 activation | Enable CO2 presence detection (RC_PresenceCO2Enable)
|  |  | CO2 level (ppm) | CO2 presence limit (RC_PresenceCO2Limit)
|  |  | CO2 hysteresis (ppm) | CO2 presence limit hysteresis (RC_PresenceCO2Hyst)
|  |  | Use internal PIR for presence | Use internal PID sensor for presence detection (RC_PIDPresence)
Extra zone
Extra zone
|  |  | Extra zone function | Extra Zone function (RC_ExtraZoneControlFunction)
|  |  | Disabled below state | Disable Extra Zone control below this controller state (RC_ExtraZoneMinControllerState)
|  |  | Disable if main zone mode differs from function | Disable Extra Zone if mode differs from room PID mode (RC_ExtraZoneDisableIfWrongMode)
|  |  | Min limit (%) | Minimum output for Extra Zone (RC_ExtraZoneOutputMin)
|  |  | Max limit (%) | Maximum output for Extra Zone (RC_ExtraZoneOutputMax)
Inputs/Outputs
Universal inputs
|  |  | UI1 | UI1 Input function (RC_UI1Func)
|  |  | UI1 NC/NO | Invert logic signal (IoDiIn_1_invert)
|  |  | UI2 | UI2 Input function (RC_UI2Func)
|  |  | UI2 NC/NO | Invert logic signal (IoDiIn_2_invert)
Universal outputs
|  |  | UO1 | UO1 Output function (RC_UO1Func)
|  |  | UO1 period thermal valve (s) | Period time for pulse output (IoAnaOut_1_pulse_period)
|  |  | UO1 NC/NO | Set to 1 to invert output (IoDo_1_invert)
|  |  | UO2 | UO2 Output function (RC_UO2Func)
|  |  | UO2 period thermal valve (s) | Period time for pulse output (IoAnaOut_2_pulse_period)
|  |  | UO2 NC/NO | Set to 1 to invert output (IoDo_2_invert)
Analog outputs
|  |  | AO1 | UO3 Output function (RC_UO3Func)
|  |  | AO2/CI | UO4 Output function (RC_UO4Func)
Fan control
Fan control source
|  |  | Room controller | Select fan control mode (RC_FanControlMode)
|  |  | CO2 level | Fan is controlled by CO2 output (RC_FanCO2Control)
|  |  | Humidity | Fan is controlled by humidity output (RC_FanControlHumidity)
EC Fan control
|  |  | Speed at no demand | Fan never stops in auto mode (RC_FanSpeedMin)
|  |  | Off below demand (%) | Min EC fan speed in % (RC_ECFanSpeedStartLimit)
|  |  | Hysteresis for fan speed decrease (%) | Hysteresis for fan speed outputs (RC_FanSpeedHyst)
|  |  | Start speed (%) | Min EC fan speed in % (RC_ECFanSpeedMin)
|  |  | Max speed in auto mode (%) | Max EC fan speed in % (RC_ECFanSpeedMax)
|  |  | Forced ventilation speed | Fan runs at RC_ECFanSpeedForced when forced ventilation is active (RC_FanForcedVentilation)
|  |  | Forced ventilation speed (%) | Forced ventilation EC fan speed (RC_ECFanSpeedForced)
|  |  | Speed 1 output (%) | EC fan speed for manual speed 1 (RC_ECFanManualSpeed1)
|  |  | Speed 2 output (%) | EC fan speed for manual speed 2 (RC_ECFanManualSpeed2)
|  |  | Speed 3 output (%) | EC fan speed for manual speed 3 (RC_ECFanManualSpeed3)
|  |  | Mould protection | Mould protect active. Fan never stops regardless of other settings (RC_FanMouldProtect)
Fan kick start
|  |  | Kick-start time (s) | Fan kick start time (RC_FanKickStartTime)
Fan off delay
|  |  | Off delay time (s) | Fan afterblow run time. 0 = Not active (RC_FanAfterblowTime)
|  |  | Minimum speed | Fan afterblow min speed (RC_FanAfterblowMinSpeed)
Fan boost
|  |  | Mode | Fan start boost heat cool select. 0=heat, 1=cool, 2=both (RC_FanBoostMode)
|  |  | Boost time (s) | Fan boost run time. 0 = Not active (RC_FanBoostRunTime)
|  |  | P-band | Fan boost P band (RC_FanBoostPBand)
Display and menus
Display
|  |  | Start screen | What to display during device startup (DisplayStartupMode)
|  |  | View mode | Select value to be shown in the display (RC_DisplayViewMode)
|  |  | Alternate temp/CO2 | Alternate temperature/CO2 display (RC_TemperatureCO2)
|  |  | Setpoint mode | Select setpoint display at setpoint adjustment (RC_DisplaySetpointMode)
|  |  | Round CO2 value to nearest | Min step for CO2 value (RC_CO2Step)
|  |  | Brightness full (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | Dim timeout, 0 = Always full (s) | Display time in full mode. 0 = Never dim. (Disp_TimeFull)
|  |  | Brightness dimmed (%) | Display brightness, dimmed (%) (Disp_BrightnessDim)
|  |  | Off timeout, 0 = Never off (s) | Display time in dimmed mode. 0 = Never off. (Disp_TimeDim)
Values to display
Timer
|  |  | Display mode | How to show the timer in the display (rt_exttime_mode)
|  |  | Animation | Show animation in timer view (rt_exttime_animate)
|  |  | Turn on LED when active | Indicate with LED if timer is active (rt_exttime_indicate)
|  |  | Step size in minutes (Minutes) | Step size in minutes for each button press (rt_exttime_step_size)
|  |  | Number of steps | Number of steps before cycling back to off (rt_exttime_steps)
|  |  | Current timer value (Minutes) | Time remaining (rt_exttime_timeleft)
|  |  | Timer state | Current timer state (rt_exttime_state)
Custom Texts
|  |  | View mode | When to show the custom text (rt_text_visability)
|  |  | Display mode | Single or dual row text in display (rt_text_mode)
|  |  | Scroll mode | Scroll mode (rt_text_display_scroll_mode)
|  |  | Font | What font to use for the display text (rt_text_font)
|  |  | Scroll delay (ms) | Time in ms between scrolling one pixel (rt_text_display_scroll_speed)
|  |  | Custom text timer value (s) | Time to show the custom text (rt_text_timeleft)
|  |  | Custom text row 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Custom text row 2 | String to show on row 2 in the display (rt_text_row_2)
|  |  | Custom text 1 | String to show on row 1 in the display (rt_text_row_1)
|  |  | Custom text 2 | String to show on row 2 in the display (rt_text_row_2)
Led indication
|  |  | Brightness (%) | Display brightness, full (%) (Disp_BrightnessFull)
|  |  | CO2 led indication | Enable/disable CO2 led indication (RC_CO2SetIndication)
|  |  | Yellow led CO2 level (ppm) | CO2 level for yellow led (RC_CO2LevelYellow)
|  |  | Red led CO2 level (ppm) | CO2 level for red led (RC_CO2LevelRed)
Menu
|  |  | Setpoint adjust | Enable setpoint setting from display (App_EnableSetpoint)
|  |  | Mode menu page | Enable Mode menu page (App_EnableMenuMode)
|  |  | Change-over menu page | Enable Change-over menu page (App_EnableMenuChangeOver)
|  |  | Fan menu page | Enable Fan menu page (App_EnableMenuFan)
|  |  | Forced ventilation menu page | Enable Forced ventilation menu page (App_EnableMenuForcedVent)
|  |  | Forced ventilation extended run | Enable forced ventilation extended run (RC_BypassExtendedRun)
|  |  | Humidity menu page | Enable Humidity menu page (App_EnableMenuHumidity)
|  |  | CO2 menu page | Enable CO2 menu page (App_EnableMenuCO2)
|  |  | VOC menu page | Enable VOC menu page (App_EnableMenuVOC)
Mode menu options
|  |  | Menu title text | Mode menu title (App_ModeMenuTitle)
|  |  | Mode Off enable | Mode menu Off state enable (App_ModeMenuOffEnable)
|  |  | Mode Unoccupied enable | Mode menu Unoccupied state enable (App_ModeMenuUnoccEnable)
|  |  | Mode Standby enable | Mode menu Standby state enable (App_ModeMenuStandbyEnable)
|  |  | Mode Occupied enable | Mode menu Occupied state enable (App_ModeMenuOccEnable)
|  |  | Mode Forced ventilation enable | Mode menu Bypass state enable (App_ModeMenuBypassEnable)
|  |  | Mode Off text | Mode menu Off state text (App_ModeMenuOffText)
|  |  | Mode Unoccupied text | Mode menu Unoccupied state text (App_ModeMenuUnoccText)
|  |  | Mode Standby text | Mode menu Standby state text (App_ModeMenuStandbyText)
|  |  | Mode Occupied text | Mode menu Occupied state text (App_ModeMenuOccText)
|  |  | Mode Forced ventilation text | Mode menu Bypass state text (App_ModeMenuBypassText)
|  |  | Mode Auto text | Mode menu Auto state text (App_ModeMenuAutoText)
Change-over menu options
|  |  | Menu title text | Change-over menu title (App_ChangeOverMenuTitle)
|  |  | State Heat enable | Change-over menu Heat state enable (App_ChangeOverMenuHeatEnable)
|  |  | State Cool enable | Change-over menu Cool state enable (App_ChangeOverMenuCoolEnable)
|  |  | State Auto enable | Change-over menu Auto state enable (App_ChangeOverMenuAutoEnable)
|  |  | State Heat text | Change-over menu Heat state text (App_ChangeOverMenuHeatText)
|  |  | State Cool text | Change-over menu Cool state text (App_ChangeOverMenuCoolText)
|  |  | State Auto text | Change-over menu Auto state text (App_ChangeOverMenuAutoText)
Actuators
On/off outputs
|  |  | Heating hysteresis, room temperature (ºC) | Room temperature heating hysteresis for thermostat (RC_RoomTempHeatHyst)
|  |  | Cooling hysteresis, room temperature (ºC) | Room temperature cooling hysteresis for thermostat (RC_RoomTempCoolHyst)
|  |  | Hysteresis, extra zone temperature (ºC) | Extra zone temperature hysteresis for thermostat (RC_ExtraZoneTempHyst)
Valve exercise
|  |  | Exercise valves | Valve exercise function (RC_ValveExerciseFunction)
|  |  | Heat interval (h) | Heat valve 1 exercise interval (hours) (RC_ValveExerciseIntervalHeat1)
|  |  | Heat 2 interval (h) | Heat valve 2 exercise interval (hours) (RC_ValveExerciseIntervalHeat2)
|  |  | Cool interval (h) | Cool valve 1 exercise interval (hours) (RC_ValveExerciseIntervalCool1)
|  |  | Cool 2 interval (h) | Cool valve 2 exercise interval (hours) (RC_ValveExerciseIntervalCool2)
|  |  | Change-over interval (h) | Change-over valve exercise interval (hours) (RC_ValveExerciseIntervalChangeOver)
|  |  | 6-way valve interval (h) | 6-way valve exercise interval (hours) (RC_ValveExerciseInterval6Way)
|  |  | Heat duration (s) | Heat valve 1 runtime (seconds) (RC_ValveRuntimeHeat1)
|  |  | Heat 2 duration (s) | Heat valve 2 runtime (seconds) (RC_ValveRuntimeHeat2)
|  |  | Cool duration (s) | Cool valve 1 runtime (seconds) (RC_ValveRuntimeCool1)
|  |  | Cool 2 duration (s) | Cool valve 2 runtime (seconds) (RC_ValveRuntimeCool2)
|  |  | Change-over duration (s) | Change-over valve runtime (seconds) (RC_ValveRuntimeChangeOver)
|  |  | 6-way valve duration (s) | 6-way valve runtime (seconds) (RC_ValveRuntime6Way)
Analog inputs
Temperature input
|  |  | Filter time (s) | Temperature filter time (0 to 17200 seconds) (RC_TempFilterTime)
Temperature input 0-10V
|  |  | Value at 0 V (°C) | Room temperature at 0 Volt input (RC_RoomTemp_0V)
|  |  | Value at 10 V (°C) | Room temperature at 10 Volt input (RC_RoomTemp_10V)
CO2 input
|  |  | Value at 0 V (ppm) | CO2 at 0 Volt input (RC_CO2_0V)
|  |  | Value at 10 V (ppm) | CO2 at 10 Volt input (RC_CO2_10V)
|  |  | Filter time (s) | CO2 filter time (0 to 17200 seconds) (RC_CO2FilterTime)
Humidity input
|  |  | Value at 0 V (%) | RH at 0 Volt input (RC_RH_0V)
|  |  | Value at 10 V (%) | RH at 10 Volt input (RC_RH_10V)
|  |  | Filter time (s) | RH filter time (0 to 17200 seconds) (RC_RHFilterTime)
Flow input
|  |  | Value at 0 V | Air flow at 0 Volt input (RC_Flow_0V)
|  |  | Value at 10 V | Air flow at 10 Volt input (RC_Flow_10V)
|  |  | Filter time (s) | Air flow filter time (0 to 17200 seconds) (RC_FlowFilterTime)
VOC input
|  |  | Value at 0 V | VOC index at 0 Volt input (RC_VOC_0V)
|  |  | Value at 10 V | VOC index at 10 Volt input (RC_VOC_10V)
|  |  | Filter time (s) | VOC index filter time (0 to 17200 seconds) (RC_VOCFilterTime)
Setpoints
Room setpoints
|  |  | Heating, occupied (°C) | Heating setpoint in Occupied state. (RC_RoomSetpointHeatOccupied)
|  |  | Cooling, occupied (°C) | Cooling setpoint in Occupied state. (RC_RoomSetpointCoolOccupied)
|  |  | Heating, standby (°C) | Heating setpoint in Standby state. (RC_RoomSetpointHeatStandby)
|  |  | Cooling, standby (°C) | Cooling setpoint in Standby state. (RC_RoomSetpointCoolStandby)
|  |  | Heating, unoccupied (°C) | Heating setpoint in Unoccupied state. (RC_RoomSetpointHeatUnoccupied)
|  |  | Cooling, unoccupied (°C) | Cooling setpoint in Unoccupied state. (RC_RoomSetpointCoolUnoccupied)
|  |  | Frost protection (°C) | Heating setpoint in Off state (frost protection). (RC_RoomSetpointHeatOff)
Setpoint adjustment
|  |  | Max up adjustment (°C) | Maximum positive setpoint offset. (RC_RoomSetpointOffsetMaxPos)
|  |  | Max down adjustment (°C) | Maximum negative setpoint offset. (RC_RoomSetpointOffsetMaxNeg)
|  |  | Setpoint adjustment (°C) | Setpoint offset. Effective in Standby state or higher. (RC_RoomSetpointOffset)
Extra zone
|  |  | Extra zone setpoint (°C) | Setpoint for Extra Zone (RC_ExtraZoneSetpoint)
CO2
|  |  | CO2 setpoint (ppm) | Setpoint for CO2 control (RC_CO2Setpoint)
Humidity
|  |  | Humidity setpoint (%) | Setpoint Humidity control (RC_HumiditySetpoint)
VOC
|  |  | VOC setpoint | Setpoint for VOC control (RC_VOCSetpoint)
Controller settings
Room
|  |  | P-band (°C) | P-band for room PID controller (RC_RoomPIDPband)
|  |  | I-time (s) | I-time for room PID controller (RC_RoomPIDItime)
Cascade control
|  |  | Control active | Function of supply air limitation (RC_SupplyAirFunction)
|  |  | Cascade factor | Conversion factor for cascade PI parameters (RC_SupplyAirCascadeFactor)
|  |  | Max heating temperature (°C) | Max supply air temperature when heating (RC_SupplyAirHeatMax)
|  |  | Min heating temperature (°C) | Min supply air temperature when heating (RC_SupplyAirHeatMin)
|  |  | Max cooling temperature (°C) | Max supply air temperature when cooling (RC_SupplyAirCoolMax)
|  |  | Min cooling temperature (°C) | Min supply air temperature when cooling (RC_SupplyAirCoolMin)
|  |  | Frost protection temperature (°C) | Min supply air temperature in frost protect (RC_SupplyAirFrostProtect)
Extra zone
|  |  | P-band (°C) | P-band for Extra Zone PID controller (RC_ExtraZonePIDPband)
|  |  | I-time (s) | I-time for Extra Zone PID controller (RC_ExtraZonePIDItime)
CO2
|  |  | P-band (ppm) | P-band for CO2 PID controller (RC_CO2PIDPband)
|  |  | I-time (s) | I-time for CO2 PID controller (RC_CO2PIDItime)
Humidity
|  |  | P-band (%) | P-band for Humidity PID controller (RC_HumidityPIDPband)
|  |  | I-time (s) | I-time for Humidity PID controller (RC_HumidityPIDItime)
VOC
|  |  | P-band | P-band for VOC PID controller (RC_VOCPIDPband)
|  |  | I-time (s) | I-time for VOC PID controller (RC_VOCPIDItime)
Alarm settings
Room temperature alarm
|  |  | High limit (°C) | High room temp alarm limit (RC_AlarmRoomTempLimitHigh)
|  |  | Low limit (°C) | Low room temp alarm limit (RC_AlarmRoomTempLimitLow)
CO2 level alarm
|  |  | High limit (ppm) | High CO2 alarm limit (RC_AlarmCO2LimitHigh)
Input adjustments
UI1
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_1_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_1_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_1_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_1_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_1_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_1_offset)
UI2
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_2_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_2_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_2_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_2_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_2_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_2_offset)
Room temperature
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_5_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_5_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_5_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_5_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_5_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_5_offset)
Room humidity
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_6_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_6_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_6_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_6_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_6_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_6_offset)
VOC sensor
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_7_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_7_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_7_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_7_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_7_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_7_offset)
CO2 sensor
|  |  | Limits mode | Use Max and Min values as limits, or set error if outside (IoAnaIn_8_limit)
|  |  | Minimum value | Scale for input (IoAnaIn_8_min_in)
|  |  | Maximum value | Scale for input (IoAnaIn_8_max_in)
|  |  | Adjusted minimum value | Scale for input (IoAnaIn_8_min_out)
|  |  | Adjusted maximum value | Scale for input (IoAnaIn_8_max_out)
|  |  | Offset adjustment | Offset for input (IoAnaIn_8_offset)
Output adjustments
UO1
|  |  | Minimum value | Scale for output (IoAnaOut_1_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_1_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_1_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_1_max_out)
|  |  | Offset based on full range [-1=-100%, 1=100%] | Offset for output (IoAnaOut_1_offset)
UO2
|  |  | Minimum value | Scale for output (IoAnaOut_2_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_2_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_2_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_2_max_out)
|  |  | Offset based on full range [-1=-100%, 1=100%] | Offset for output (IoAnaOut_2_offset)
AO1
|  |  | Minimum value | Scale for output (IoAnaOut_3_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_3_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_3_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_3_max_out)
|  |  | Offset based on full range [-1=-100%, 1=100%] | Offset for output (IoAnaOut_3_offset)
AO2
|  |  | Minimum value | Scale for output (IoAnaOut_4_min_in)
|  |  | Maximum value | Scale for output (IoAnaOut_4_max_in)
|  |  | Minimum value [0=0%, 100=100%] | Scale for output (IoAnaOut_4_min_out)
|  |  | Maximum value [0=0%, 100=100%] | Scale for output (IoAnaOut_4_max_out)
|  |  | Offset based on full range [-1=-100%, 1=100%] | Offset for output (IoAnaOut_4_offset)
Manual/Auto
Remote input values
Room temperature
|  |  | Remote setting | Enable remote setting of room temperature (RC_RoomTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of room temperature (RC_RoomTempRemote)
|  |  | Room temperature (°C) | Room temperature (RC_RoomTemp)
Supply air temperature
|  |  | Remote setting | Enable remote setting of supply air temperature (RC_SupplyAirTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of supply air temperature (RC_SupplyAirTempRemote)
|  |  | Supply air temperature (°C) | Supply air temperature (RC_SupplyAirTemp)
Extra zone temperature
|  |  | Remote setting | Enable remote setting of extra zone temperature (RC_ExtraZoneTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of extra zone temperature (RC_ExtraZoneTempRemote)
|  |  | Extra zone temperature (°C) | Extra Zone temperature (RC_ExtraZoneTemp)
Change-over temperature
|  |  | Remote setting | Enable remote setting of changeover temperature (RC_ChangeOverTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of changeover temperature (RC_ChangeOverTempRemote)
|  |  | Change-over temperature (°C) | Changeover temperature (RC_ChangeOverTemp)
Change-over VAV temperature
|  |  | Remote setting | Enable remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemoteSelect)
|  |  | Set value (°C) | Remote setting of changeover VAV temperature (RC_ChangeOverVAVTempRemote)
|  |  | Change-over VAV temperature (°C) | Changeover VAV temperature (RC_ChangeOverVAVTemp)
CO2 level
|  |  | Remote setting | Enable remote setting of room CO2 level (RC_CO2LevelRemoteSelect)
|  |  | Set value (ppm) | Remote setting of room CO2 level (RC_CO2LevelRemote)
|  |  | CO2 level (ppm) | Room CO2 level (RC_CO2Level)
Room humidity
|  |  | Remote setting | Enable remote setting of relative humidity (RC_HumidityRemoteSelect)
|  |  | Set value (%) | Remote setting of relative humidity (RC_HumidityRemote)
|  |  | Room humidity (%) | Relative humidity (RC_Humidity)
Air Flow
|  |  | Remote setting | Enable remote setting of air flow (RC_AirFlowRemoteSelect)
|  |  | Set value | Remote setting of air flow (RC_AirFlowRemote)
|  |  | Air Flow | Air flow (RC_AirFlow)
VOC index
|  |  | Remote setting | Enable remote setting of VOC index (RC_VOCRemoteSelect)
|  |  | Set value | Remote setting of VOC index (RC_VOCRemote)
|  |  | VOC index | VOC index (RC_VOC)
Presence detection
|  |  | Remote setting | Enable remote setting of presence digital input (RC_DIPresenceRemoteSelect)
|  |  | Set value | Remote setting of presence digital input (RC_DIPresenceRemote)
|  |  | Presence detection | Presence indication (RC_Presence)
Open window
|  |  | Remote setting | Enable remote setting of window contact digital input (RC_DIOpenWindowRemoteSelect)
|  |  | Set value | Remote setting of window contact digital input (RC_DIOpenWindowRemote)
|  |  | Open window | Open window indication (RC_DIOpenWindow)
Condensation
|  |  | Remote setting | Enable remote setting of condensation digital input (RC_DICondensationRemoteSelect)
|  |  | Set value | Remote setting of condensation digital input (RC_DICondensationRemote)
|  |  | Condensation | Condensation indication (RC_DICondensation)
External alarm (DI)
|  |  | Remote setting | Enable remote setting of alarm digital input (RC_DIAlarmRemoteSelect)
|  |  | Set value | Remote setting of alarm digital input (RC_DIAlarmRemote)
|  |  | External alarm (DI) | Digital input alarm (RC_AlarmDI)
Change-over DI
|  |  | Remote setting | Enable remote setting of change over digital input (RC_DIChangeoverRemoteSelect)
|  |  | Set value | Remote setting of change over digital input (RC_DIChangeoverRemote)
|  |  | Change-over DI | Change-over digital input (RC_DIChangeOver)
Change-over VAV DI
|  |  | Remote setting | Enable remote setting of change over VAV digital input (RC_DIChangeoverVAVRemoteSelect)
|  |  | Set value | Remote setting of change over VAV digital input (RC_DIChangeoverVAVRemote)
|  |  | Change-over VAV DI | Change-over VAV digital input (RC_DIChangeOverVAV)
Manual/Auto
Controller state
|  |  | Controller state | Current state (RC_ControllerState)
|  |  | Remote state setting | Sets the state directly via communication. (RC_RemoteControllerState)
|  |  | Shutdown | Set controller in the state indicated by RC_ControllerStateShutdown (RC_ControllerStateSetShutdown)
|  |  | Forced ventilation | Set controller in Bypass state (RC_ControllerStateSetBypass)
Fan control source
|  |  | Fan control source | Fan speed setting (RC_FanSelect)
Heating output
|  |  | Mode | Manual/auto select for RoomHeat1Output (RC_RoomHeat1OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomHeat1Output (RC_RoomHeat1OutputManual)
|  |  | Heating output (%) | Room control Heat1 output analog (RC_RoomHeat1OutputAO)
|  |  | Mode | Manual/auto select Heat1 output digital (RC_RoomHeat1OutputManSelectDO)
|  |  | Heating output | Room control Heat1 output digital (RC_RoomHeat1OutputDO)
Heating 2 output
|  |  | Mode | Manual/auto select for RoomHeat2Output (RC_RoomHeat2OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomHeat2Output (RC_RoomHeat2OutputManual)
|  |  | Heating 2 output (%) | Room control Heat2 output analog (RC_RoomHeat2OutputAO)
|  |  | Mode | Manual/auto select Heat2 output digital (RC_RoomHeat2OutputManSelectDO)
|  |  | Heating 2 output | Room control Heat2 output digital (RC_RoomHeat2OutputDO)
Cooling output
|  |  | Mode | Manual/auto select for RoomCool1Output (RC_RoomCool1OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomCool1Output (RC_RoomCool1OutputManual)
|  |  | Cooling output (%) | Room control Cool1 output analog (RC_RoomCool1OutputAO)
|  |  | Mode | Manual/auto select Cool1 output digital (RC_RoomCool1OutputManSelectDO)
|  |  | Cooling output | Room control Cool1 output digital (RC_RoomCool1OutputDO)
Cooling 2 output
|  |  | Mode | Manual/auto select for RoomCool2Output (RC_RoomCool2OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomCool2Output (RC_RoomCool2OutputManual)
|  |  | Cooling 2 output (%) | Room control Cool2 output analog (RC_RoomCool2OutputAO)
|  |  | Mode | Manual/auto select Cool2 output digital (RC_RoomCool2OutputManSelectDO)
|  |  | Cooling 2 output | Room control Cool2 output digital (RC_RoomCool2OutputDO)
VAV output
|  |  | Mode | Manual/auto select for RoomVAV1Output (RC_RoomVAV1OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomVAV1Output (RC_RoomVAV1OutputManual)
|  |  | VAV output (%) | Room control VAV1 output analog (RC_RoomVAV1OutputAO)
VAV 2 output
|  |  | Mode | Manual/auto select for RoomVAV2Output (RC_RoomVAV2OutputManSelect)
|  |  | Set value (%) | Manual setting of RoomVAV2Output (RC_RoomVAV2OutputManual)
|  |  | VAV 2 output (%) | Room control VAV2 output analog (RC_RoomVAV2OutputAO)
Change-over output
|  |  | Mode | Manual/auto select for RoomChangeOverOutput (RC_RoomChangeOverOutputManSelect)
|  |  | Set value (%) | Manual setting of RoomChangeOverOutput (RC_RoomChangeOverOutputManual)
|  |  | Change-over output (%) | Room control Change over output analog (RC_RoomChangeOverOutputAO)
Change-over VAV output
|  |  | Mode | Manual/auto select for RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManSelect)
|  |  | Set value (%) | Manual setting of RoomChangeOverVAVOutput (RC_RoomChangeOverVAVOutputManual)
|  |  | Change-over VAV output (%) | Room control Change over VAV output analog (RC_RoomChangeOverVAVOutputAO)
6-way valve output
|  |  | Mode | Manual/auto select for Room6WayValveOutput (RC_Room6WayValveOutputManSelect)
|  |  | Mode | Manual setting of 6-way valve heat/cool (RC_Room6WayValveOutputHeatCool)
|  |  | Set value (%) | Manual setting of Room6WayValveOutput (RC_Room6WayValveOutputManual)
|  |  | 6-way valve output (%) | Room control 6-way valve output analog (RC_Room6WayValveOutputAO)
Extra zone output
|  |  | Mode | Manual/auto select for ExtraZoneOutput (RC_ExtraZoneOutputManSelect)
|  |  | Set value (%) | Manual setting of ExtraZoneOutput (RC_ExtraZoneOutputManual)
|  |  | Extra zone output | Extra Zone output analog (RC_ExtraZoneOutputAO)
EC Fan control
|  |  | Mode | Manual/auto select for ECFanSpeed (RC_ECFanSpeedManSelect)
|  |  | Set value (%) | Manual setting of ECFanSpeed (RC_ECFanSpeedManual)
|  |  | EC Fan control (%) | Current EC fan speed (RC_ECFanSpeed)
CO2 control output
|  |  | Mode | Manual/auto select for CO2Control (RC_CO2ControlManSelect)
|  |  | Set value (%) | Manual setting of CO2Control (RC_CO2ControlManual)
|  |  | CO2 control output (%) | CO2 control analog out (RC_CO2ControlAO)
Humidify control output
|  |  | Mode | Manual/auto select for HumidifyOutput (RC_HumidifyOutputManSelect)
|  |  | Set value (%) | Manual setting of HumidifyOutput (RC_HumidifyOutputManual)
|  |  | Humidify control output (%) | Humidify analog out (RC_HumidifyOutputAO)
Dehumidify control output
|  |  | Mode | Manual/auto select for DehumidifyOutput (RC_DehumidifyOutputManSelect)
|  |  | Set value (%) | Manual setting of DehumidifyOutput (RC_DehumidifyOutputManual)
|  |  | Dehumidify control output (%) | Dehumidify analog out (RC_DehumidifyOutputAO)
VOC control output
|  |  | Mode | Manual/auto select for VOCControl (RC_VOCControlManSelect)
|  |  | Set value (%) | Manual setting of VOCControl (RC_VOCControlManual)
|  |  | VOC control output (%) | VOC control analog out (RC_VOCControlAO)
Extra zone active output
|  |  | Mode | Manual/auto select Extra Zone active digital out (RC_ExtraZoneActiveManSelectDO)
|  |  | Extra zone active output | Extra Zone active (RC_ExtraZoneActive)
Forced ventilation output
|  |  | Mode | Manual/auto select Forced Ventilation digital out (RC_ForcedVentilationManSelectDO)
|  |  | Forced ventilation output | Forced ventilation output (RC_ForcedVentDO)
Hardware control
UO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_1_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_1_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_1_override)
|  |  | UO1: | Value set for output (IoDo_1_value)
|  |  | Mode | Set to 1 to enable override (IoDo_1_override_en)
|  |  | Set value | Override value (IoDo_1_override)
UO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_2_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_2_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_2_override)
|  |  | UO1: | Value set for output (IoDo_2_value)
|  |  | Mode | Set to 1 to enable override (IoDo_2_override_en)
|  |  | Set value | Override value (IoDo_2_override)
AO1
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_3_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_3_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_3_override)
AO2
|  |  | UO1: (V) | Actual value on the output pin in Volt or milliampere. (IoAnaOut_4_converted)
|  |  | Mode | Set to 1 to enable override (IoAnaOut_4_override_en)
|  |  | Set value [0=0%, 100=100%] | Override value (IoAnaOut_4_override)
UI1
|  |  | UI1 | Filtered value from sensor (IoAnaIn_1_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_1_override_en)
|  |  | Set value | Override value (IoAnaIn_1_override)
UI2
|  |  | UI2 | Filtered value from sensor (IoAnaIn_2_value)
|  |  | Mode | Set to 1 to enable override (IoAnaIn_2_override_en)
|  |  | Set value | Override value (IoAnaIn_2_override)
*** Text not found ***
|  |  | *** Text not found *** | Enable automatic calibration of CO2 sensor (SCD40_ASC_enable)
|  |  | *** Text not found *** (ppm) | Automatic calibration of CO2 sensor target (SCD40_ASC_target)
|  |  | *** Text not found *** | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done (SCD40_FRC_enable)
|  |  | *** Text not found *** (ppm) | Current actual CO2 value to calibrate to (SCD40_FRC_target)
|  |  | *** Text not found *** | Calculated offset after calibration or -9999 if failed. (SCD40_FRC_result)
|  |  | *** Text not found *** | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset (SCD40_factory_reset)
Relay output
|  |  | Relay state | Value set for output (IoDo_3_value)
|  |  | Mode | Set to 1 to enable override (IoDo_3_override_en)
|  |  | Set value | Override value (IoDo_3_override)
Device
Controller ID
Controller ID
|  |  | Name | (ControllerName)
|  |  | Description | Controller description (ControllerDescription)
|  |  | Location | Controller location (ControllerLocation)
|  |  | Project | (ControllerProject)
Communication
Port settings
|  |  | Port 1 function | Comm. protocol Port 1 (RS485) (RC_Port1Mode)
|  |  | Port 1 baudrate | Comm. speed Port 1 (RS485) (RC_Port1Baud)
|  |  | Port 1 parity | Comm. format Port 1 (RS485) (RC_Port1Format)
Exoline
|  |  | PLA | (PLA)
|  |  | ELA | (ELA)
Modbus
|  |  | Modbus address | Active Modbus unit ID (ModbusUnitID)
BACnet
|  |  | BACnet MSTP address | BACnet MS/TP MAC port 1 (BACnetMstpMAC_Port_1)
|  |  | MSTP max master address | BACnet MS/TP max master address port 1 (BACnetMstpMaxMasterAddr_Port_1)
|  |  | BACnet device ID | BACnet device ID (BACnetDeviceID)
|  |  | BACnet device object name | BACnet device object name (BACnetDeviceObjectName)
|  |  | Password | BACnet password (BACnetPassword)
Bluetooth
|  |  | Bluetooth function | Function for BLE button (BleButtonMode)
|  |  | Turn off after (s) | Timeout when BLE is started with the button (BleButtonTimeout)
Communication fail
|  |  | Fail action | Offline function (RC_OfflineFunction)
|  |  | Timeout (s) | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. (RC_OfflineTimeout)
|  |  | Fallback state | State to set during communication faults (RC_ControllerStateFail)
|  |  | Status | Heartbeat function indicates if the device is offline or not (RC_Offline)
Reset
Reset
|  |  | Restart controller | Write to this register will trigger resets with different reset reasons (product_reset)