## Variables
RCX-… - Variable list | [12 empty] | Revision: | 1.0-1-00
|  |  | EXOline |  |  | Modbus |  |  |  | BACnet
Name | Default | Description | Type | Load | Cell | Register type | Address | Scale | Offset | Object type | Instance | Unit | Writeable | Variable type
ModbusListVersion |  | Modbus list version | X | 1 | 0 | Input | 1
product_reset | 0 | Write to this register will trigger resets with different reset reasons | I | 1 | 1 | Holding | 1 |  |  | positive_integer_value | 9001 |  | X
rc_wink | 0 | Wink for this amount of time in seconds | X | 1 | 3 | Holding | 3 |  |  | positive_integer_value | 9011 |  | X
RC_CommSettingsCommit | 0 | Commit communication settings | L | 1 | 5 | Coil | 1 |  |  | binary_value | 9001 |  | X
RC_Port1Mode | 21 | Comm. protocol Port 1 (RS485) | X | 1 | 6 | Holding | 5 |  |  | multi_state_value | 9001 |  | X
RC_Port1Baud | 0 | Comm. speed Port 1 (RS485) | X | 1 | 7 | Holding | 7 |  |  | multi_state_value | 9101 |  | X
RC_Port1Format | 112 | Comm. format Port 1 (RS485) | X | 1 | 8 | Holding | 6 |  |  | multi_state_value | 9201 |  | X
SerialHigh |  | Serial number, high part | I | 1 | 15 | Input | 5
SerialMid |  | Serial number, mid part | I | 1 | 17 | Input | 4
SerialLow |  | Serial number, low part | I | 1 | 19 | Input | 3
RC_Offline |  | Heartbeat function indicates if the device is offline or not | L | 1 | 21 | Discrete | 1
RC_OfflineTrigger | 0 | Write 1 to this register periodically for keep system running in normal mode, will be set to 0 by application | L | 1 | 22 | Coil | 2 |  |  | binary_value | 9101 |  | X
RC_OfflineFunction | 0 | Offline function | X | 1 | 23 | Holding | 20 |  |  | multi_state_value | 9301 |  | X
RC_OfflineCounter |  | Offline timeout counter seconds. Used to check current state of the counter, it counts from 0 at trigger up to next trigger or HEARTBEAT_OFFLINE_TIMEOUT. | I | 1 | 24 | Input | 10
RC_OfflineTimeout | 10 | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. | I | 1 | 26 | Holding | 21
RgbEnable | 0 | Set to True to enable the external control of the LED | L | 1 | 35 | Coil | 3
RgbOffColor | 0 | 8 bit color for when the LED is in state Off (0bRRRGGGBB) | X | 1 | 36 | Holding | 27
RgbOffTime | 500 | Off time in ms | I | 1 | 37 | Holding | 28
RgbOnColor | 252 | 8 bit color for when the LED is in state On (0bRRRGGGBB) | X | 1 | 39 | Holding | 29
RgbOnTime | 100 | On time in ms | I | 1 | 40 | Holding | 30
SettingsSwitch |  | Status of the rotary settings switch during boot of device | X | 1 | 57 | Input | 12
product_status | 0 | Bit field, See Description on Global device Status | I | 1 | 58 | Holding | 4
OspreyVerMajor |  | Osprey version, major part | X | 1 | 64 | Input | 13
OspreyVerMinor |  | Osprey version, minor part | X | 1 | 65 | Input | 14
OspreyVerBranch |  | Osprey version, branch part | X | 1 | 66 | Input | 15
OspreyVerNumber |  | Osprey version, number part | X | 1 | 67 | Input | 16
OspreyGitCommit |  | Osprey Git commit | I | 1 | 68 | Input | 17
OsId |  | Application OPERATING_SYSTEM_ID | I | 1 | 70 | Input | 21
Pcb_Number |  | PCB Number | I | 1 | 72 | Input | 18
Pcb_Layout |  | PCB Layout version | X | 1 | 74 | Input | 19
Pcb_BOM |  | PCB BOM version | X | 1 | 75 | Input | 20
VersionNumberString |  | The application version as a string | $ | 1 | 76
gitCommitHashString |  | The Full Git hash of the application | $ | 1 | 79
AdcCalibration | 0 | Used to trigger adc calibration | X | 1 | 82
BleButtonMode | 3 | Function for BLE button | X | 1 | 83 | Holding | 71
BleButtonTimeout | 120 | Timeout when BLE is started with the button | I | 1 | 84 | Holding | 72
model_features0 | 47990271 | Bitfield for model features | H | 1 | 86
model_features1 | 0 | Bitfield for model features | H | 1 | 89
model_features2 | 0 | Bitfield for model features | H | 1 | 92
model_features3 | 0 | Bitfield for model features | H | 1 | 95
BleVerMajor |  | BLE stack version, major part | X | 1 | 98 | Input | 22
BleVerMinor |  | BLE stack version, minor part | X | 1 | 99 | Input | 23
BleVerBranch |  | BLE stack version, branch part | X | 1 | 100 | Input | 24
BleVerNumber |  | BLE stack version, number part | X | 1 | 101 | Input | 25
FusVerMajor |  | FUS stack version, major part | X | 1 | 102 | Input | 26
FusVerMinor |  | FUS version, minor part | X | 1 | 103 | Input | 27
FusVerBranch |  | FUS version, branch part | X | 1 | 104 | Input | 28
FusVerNumber |  | FUS version, number part | X | 1 | 105 | Input | 29
RC_RoomTemp |  | Room temperature | R | 2 | 0 | Input | 5001 | 10 | 0 | analog_value | 10001 | degrees_celsius
RC_CO2Level |  | Room CO2 level | R | 2 | 3 | Input | 5002 | 1 | 0 | analog_value | 10011 | parts_per_million
RC_AirFlow |  | Air flow | R | 2 | 6 | Input | 5003 | 1 | 0 | analog_value | 10021 | REG_FLOW_UNIT
RC_ChangeOverTemp |  | Changeover temperature | R | 2 | 9 | Input | 5004 | 10 | 0 | analog_value | 10031 | degrees_celsius
RC_ChangeOverVAVTemp |  | Changeover VAV temperature | R | 2 | 12 | Input | 5005 | 10 | 0 | analog_value | 10041 | degrees_celsius
RC_ExtraZoneTemp |  | Extra Zone temperature | R | 2 | 15 | Input | 5006 | 10 | 0 | analog_value | 10051 | degrees_celsius
RC_SupplyAirTemp |  | Supply air temperature | R | 2 | 18 | Input | 5007 | 10 | 0 | analog_value | 10061 | degrees_celsius
RC_Humidity |  | Relative humidity | R | 2 | 21 | Input | 5008 | 10 | 0 | analog_value | 10071 | percent_relative_humidity
RC_Presence |  | Presence indication | L | 2 | 24 | Discrete | 5001 |  |  | binary_value | 10001
RC_DIPresence |  | DI Presence indication | L | 2 | 25 | Discrete | 5002 |  |  | binary_value | 10011
RC_CO2Presence |  | CO2 Presence indication | L | 2 | 26 | Discrete | 5003 |  |  | binary_value | 10021
RC_DIOpenWindow |  | Open window indication | L | 2 | 27 | Discrete | 5004 |  |  | binary_value | 10031
RC_DIChangeOver |  | Change-over digital input | L | 2 | 28 | Discrete | 5005 |  |  | binary_value | 10041
RC_DIChangeOverVAV |  | Change-over VAV digital input | L | 2 | 29 | Discrete | 5006 |  |  | binary_value | 10051
RC_DICondensation |  | Condensation indication | L | 2 | 30 | Discrete | 5007 |  |  | binary_value | 10061
RC_RoomActiveSetpoint |  | Active room control setpoint | R | 2 | 31 | Input | 5009 | 10 | 0 | analog_value | 10081 | degrees_celsius
RC_SupplyAirSetpoint |  | Active supply air setpoint | R | 2 | 34 | Input | 5010 | 10 | 0 | analog_value | 10091 | degrees_celsius
RC_ControllerState |  | Current state | X | 2 | 37 | Input | 5011 |  |  | multi_state_value | 10001
RC_ControllerMode |  | Current controller mode | X | 2 | 38 | Input | 5012 |  |  | multi_state_value | 10011
RC_ChangeOverState |  | Change-over status | L | 2 | 39 | Discrete | 5008 |  |  | binary_value | 10071
RC_ChangeOverStateVAV |  | Change-over VAV status | L | 2 | 40 | Discrete | 5009 |  |  | binary_value | 10081
RC_ExtraZoneActive |  | Extra Zone active | L | 2 | 41 | Discrete | 5010 |  |  | binary_value | 10091
RC_RoomHeat1OutputAO |  | Room control Heat1 output analog | X | 2 | 42 | Input | 5013 |  |  | analog_value | 10101 | percent
RC_RoomCool1OutputAO |  | Room control Cool1 output analog | X | 2 | 43 | Input | 5014 |  |  | analog_value | 10111 | percent
RC_RoomVAV1OutputAO |  | Room control VAV1 output analog | X | 2 | 44 | Input | 5015 |  |  | analog_value | 10121 | percent
RC_RoomHeat2OutputAO |  | Room control Heat2 output analog | X | 2 | 45 | Input | 5016 |  |  | analog_value | 10131 | percent
RC_RoomCool2OutputAO |  | Room control Cool2 output analog | X | 2 | 46 | Input | 5017 |  |  | analog_value | 10141 | percent
RC_RoomVAV2OutputAO |  | Room control VAV2 output analog | X | 2 | 47 | Input | 5018 |  |  | analog_value | 10151 | percent
RC_RoomChangeOverOutputAO |  | Room control Change over output analog | X | 2 | 48 | Input | 5019 |  |  | analog_value | 10161 | percent
RC_Room6WayValveOutputAO |  | Room control 6-way valve output analog | X | 2 | 49 | Input | 5020 |  |  | analog_value | 10171 | percent
RC_RoomChangeOverVAVOutputAO |  | Room control Change over VAV output analog | X | 2 | 50 | Input | 5021 |  |  | analog_value | 10181 | percent
RC_ExtraZoneOutputAO |  | Extra Zone output analog | X | 2 | 51 | Input | 5022 |  |  | analog_value | 10191 | percent
RC_ECFanSpeed |  | Current EC fan speed | X | 2 | 52 | Input | 5023 |  |  | analog_value | 10201 | percent
RC_CO2ControlAO |  | CO2 control analog out | X | 2 | 53 | Input | 5024 |  |  | analog_value | 10211 | percent
RC_HumidifyOutputAO |  | Humidify analog out | X | 2 | 54 | Input | 5025 |  |  | analog_value | 10221 | percent
RC_DehumidifyOutputAO |  | Dehumidify analog out | X | 2 | 55 | Input | 5026 |  |  | analog_value | 10231 | percent
RC_AirflowControlAO |  | Airflow control analog out | X | 2 | 56 | Input | 5027
RC_PIDHeatDemand |  | Room PID heat output | X | 2 | 57 | Input | 5028 |  |  | analog_value | 10241 | percent
RC_PIDCoolDemand |  | Room PID cool output | X | 2 | 58 | Input | 5029 |  |  | analog_value | 10251 | percent
RC_RoomHeat1OutputDO |  | Room control Heat1 output digital | L | 2 | 59 | Discrete | 5011 |  |  | binary_value | 10101
RC_RoomCool1OutputDO |  | Room control Cool1 output digital | L | 2 | 60 | Discrete | 5012 |  |  | binary_value | 10111
RC_RoomVAV1OutputDO |  | Room control VAV1 output digital | L | 2 | 61 | Discrete | 5013 |  |  | binary_value | 10121
RC_RoomHeat2OutputDO |  | Room control Heat2 output digital | L | 2 | 62 | Discrete | 5014 |  |  | binary_value | 10131
RC_RoomCool2OutputDO |  | Room control Cool2 output digital | L | 2 | 63 | Discrete | 5015 |  |  | binary_value | 10141
RC_RoomVAV2OutputDO |  | Room control VAV2 output digital | L | 2 | 64 | Discrete | 5016 |  |  | binary_value | 10151
RC_RoomChangeOverOutputDO |  | Room control Change over output digital | L | 2 | 65 | Discrete | 5017 |  |  | binary_value | 10161
RC_Room6WayValveOutputDO |  | Room control 6-way valve output digital | L | 2 | 66 | Discrete | 5018 |  |  | binary_value | 10171
RC_RoomChangeOverVAVOutputDO |  | Room control Change over VAV output digital | L | 2 | 67 | Discrete | 5019 |  |  | binary_value | 10181
RC_ExtraZoneOutputDO |  | Extra Zone output digital | L | 2 | 68 | Discrete | 5020 |  |  | binary_value | 10191
RC_CO2ControlDO |  | CO2 control digital out | L | 2 | 69 | Discrete | 5021 |  |  | binary_value | 10201
RC_HumidifyOutputDO |  | Humidify digital out | L | 2 | 70 | Discrete | 5022 |  |  | binary_value | 10211
RC_DehumidifyOutputDO |  | Dehumidify digital out | L | 2 | 71 | Discrete | 5023 |  |  | binary_value | 10221
RC_AirflowControlDO |  | Airflow control digital out | L | 2 | 72 | Discrete | 5024
RC_FanSpeed |  | Current 3-speed fan speed | X | 2 | 73 | Input | 5030
RC_FanSpeed1DO |  | Fan speed 1 output | L | 2 | 74 | Discrete | 5025
RC_FanSpeed2DO |  | Fan speed 2 output | L | 2 | 75 | Discrete | 5026
RC_FanSpeed3DO |  | Fan speed 3 output | L | 2 | 76 | Discrete | 5027
RC_ForcedVentDO |  | Forced ventilation output | L | 2 | 77 | Discrete | 5028 |  |  | binary_value | 10231
RC_AlarmRoomTempHigh |  | High room temp alarm | L | 2 | 78 | Discrete | 5029 |  |  | binary_value | 10241
RC_AlarmRoomTempLow |  | Low room temp alarm | L | 2 | 79 | Discrete | 5030 |  |  | binary_value | 10251
RC_AlarmCO2High |  | High CO2 alarm | L | 2 | 80 | Discrete | 5031 |  |  | binary_value | 10261
RC_DamperPosition |  | Damper position | R | 2 | 81 | Input | 5031 | 10 | 0 | analog_value | 10261
RC_ExtractTemperature |  | Extract temperature | R | 2 | 84 | Input | 5032 | 10 | 0 | analog_value | 10271 | degrees_celsius
RC_VOC |  | VOC index | R | 2 | 87 | Input | 5033 | 10 | 0 | analog_value | 10281
RC_DisplayViewValue |  | Value to be shown in the display | R | 2 | 90 | Input | 5034 | 10 | 0 | analog_value | 10291
RC_DisplaySetpointValue |  | Setpoint display at setpoint adjustment | R | 2 | 93 | Input | 5035 | 10 | 0 | analog_value | 10301
RC_CO2Indicator |  | RGB CO2 indication | X | 2 | 96 | Input | 5036 |  |  | multi_state_value | 10021
RC_LightingDO |  | Light control output | L | 2 | 97 | Discrete | 5032
RC_SumAlarm |  | Sum Alarm | L | 2 | 98 | Discrete | 5033 |  |  | binary_value | 10271
RC_CO2LevelRounded |  | Rounded room CO2 level | R | 2 | 99 | Input | 5037 | 1 | 0 | analog_value | 10311 | parts_per_million
RC_VOCControlAO |  | VOC control analog out | X | 2 | 102 | Input | 5038 |  |  | analog_value | 10321 | percent
RC_VOCControlDO |  | VOC control digital out | L | 2 | 103 | Discrete | 5034 |  |  | binary_value | 10281
RC_AlarmSensorError |  | Sensor error alarm | L | 2 | 104 | Discrete | 5035 |  |  | binary_value | 10291
RC_AlarmDI |  | Digital input alarm | L | 2 | 105 | Discrete | 5036 |  |  | binary_value | 10301
RC_AlarmManualOutput |  | Alarm when an output is set to manual | L | 2 | 106 | Discrete | 5037 |  |  | binary_value | 10311
RC_UI1Func | 0 | UI1 Input function | X | 3 | 0 | Holding | 5001
RC_UI2Func | 0 | UI2 Input function | X | 3 | 1 | Holding | 5002
RC_UI3Func | 0 | UI3 Input function | X | 3 | 2 | Holding | 5003
RC_UI4Func | 0 | UI4 Input function | X | 3 | 3 | Holding | 5004
RC_UO1Func | 0 | UO1 Output function | X | 3 | 20 | Holding | 5021
RC_UO2Func | 0 | UO2 Output function | X | 3 | 21 | Holding | 5022
RC_UO3Func | 0 | UO3 Output function | X | 3 | 22 | Holding | 5023
RC_UO4Func | 0 | UO4 Output function | X | 3 | 23 | Holding | 5024
RC_RoomSeq1Function | 0 | Room sequence step 1 function | X | 3 | 100 | Holding | 5101
RC_RoomSeq2Function | 0 | Room sequence step 2 function | X | 3 | 101 | Holding | 5102
RC_RoomSeq3Function | 0 | Room sequence step 3 function | X | 3 | 102 | Holding | 5103
RC_Heat1OutputMax | 100 | Heat1 maximum output for all controller states. | X | 3 | 103 | Holding | 5104
RC_Heat2OutputMax | 100 | Heat2 maximum output for all controller states. | X | 3 | 104 | Holding | 5105
RC_Heat1OutputMin | 0 | Heat1 minimum output for all controller states. | X | 3 | 105 | Holding | 5106
RC_Heat2OutputMin | 0 | Heat2 minimum output for all controller states. | X | 3 | 106 | Holding | 5107
RC_Heat1Afterblow | 0 | Heat1 enable afterblow function | L | 3 | 107 | Coil | 5001
RC_Heat2Afterblow | 0 | Heat2 enable afterblow function | L | 3 | 108 | Coil | 5002
RC_Cool1OutputMax | 100 | Cool1 maximum output for all controller states. | X | 3 | 109 | Holding | 5108
RC_Cool2OutputMax | 100 | Cool2 maximum output for all controller states. | X | 3 | 110 | Holding | 5109
RC_Cool1OutputMin | 0 | Cool1 minimum output for all controller states. | X | 3 | 111 | Holding | 5110
RC_Cool2OutputMin | 0 | Cool2 minimum output for all controller states. | X | 3 | 112 | Holding | 5111
RC_Cool1OutputMaxWhenForced | 0 | Set Cool1 output to max value when forced ventilation is active | L | 3 | 113 | Coil | 5003
RC_Cool2OutputMaxWhenForced | 0 | Set Cool2 output to max value when forced ventilation is active | L | 3 | 114 | Coil | 5004
RC_VAV1OutputMax | 100 | VAV1 maximum output for all controller states. | X | 3 | 115 | Holding | 5112
RC_VAV2OutputMax | 100 | VAV2 maximum output for all controller states. | X | 3 | 116 | Holding | 5113
RC_VAV1OutputMinOff | 0 | VAV1 minimum output in Off state. | X | 3 | 117 | Holding | 5114
RC_VAV2OutputMinOff | 0 | VAV2 minimum output in Off state. | X | 3 | 118 | Holding | 5115
RC_VAV1OutputMinUnoccupied | 10 | VAV1 minimum output in Unoccupied state. | X | 3 | 119 | Holding | 5116
RC_VAV2OutputMinUnoccupied | 10 | VAV2 minimum output in Unoccupied state. | X | 3 | 120 | Holding | 5117
RC_VAV1OutputMinStandby | 10 | VAV1 minimum output in Standby state. | X | 3 | 121 | Holding | 5118
RC_VAV2OutputMinStandby | 10 | VAV2 minimum output in Standby state. | X | 3 | 122 | Holding | 5119
RC_VAV1OutputMinOccupied | 20 | VAV1 minimum output in Occupied state | X | 3 | 123 | Holding | 5120
RC_VAV2OutputMinOccupied | 20 | VAV2 minimum output in Occupied state | X | 3 | 124 | Holding | 5121
RC_VAV1OutputMinBypass | 20 | VAV1 minimum output in Bypass state. | X | 3 | 125 | Holding | 5122
RC_VAV2OutputMinBypass | 20 | VAV2 minimum output in Bypass state. | X | 3 | 126 | Holding | 5123
RC_VAV1OutputMaxWhenForced | 0 | Set VAV1 output to max value when forced ventilation is active | L | 3 | 127 | Coil | 5005
RC_VAV2OutputMaxWhenForced | 0 | Set VAV2 output to max value when forced ventilation is active | L | 3 | 128 | Coil | 5006
RC_VAV1OutputMaxHeat | 0 | VAV1 maximum output when the controller is in heating mode. | X | 3 | 129 | Holding | 5124
RC_ChangeOverVAVOutputMax | 100 | ChangeOverVAV maximum output for all controller states. | X | 3 | 130 | Holding | 5125
RC_ChangeOverVAVOutputMinOff | 0 | ChangeOverVAV minimum output in Off state. | X | 3 | 131 | Holding | 5126
RC_ChangeOverVAVOutputMinUnoccupied | 10 | ChangeOverVAV minimum output in Unoccupied state. | X | 3 | 132 | Holding | 5127
RC_ChangeOverVAVOutputMinStandby | 10 | ChangeOverVAV minimum output in Standby state. | X | 3 | 133 | Holding | 5128
RC_ChangeOverVAVOutputMinOccupied | 20 | ChangeOverVAV minimum output in Occupied state | X | 3 | 134 | Holding | 5129
RC_ChangeOverVAVOutputMinBypass | 20 | ChangeOverVAV minimum output in Bypass state. | X | 3 | 135 | Holding | 5130
RC_ChangeOverVAVOutputMaxWhenForced | 0 | Set ChangeOverVAV output to max value when forced ventilation is active | L | 3 | 136 | Coil | 5007
RC_VAVControlCooling | 1 | VAV is controlled by cooling output | L | 3 | 137 | Coil | 5008
RC_VAVControlCO2 | 0 | VAV is controlled by CO2 output | L | 3 | 138 | Coil | 5009
RC_ChangeOverOutputMax | 100 | Changeover maximum output for all controller states. | X | 3 | 141 | Holding | 5131
RC_ChangeOverOutputMin | 0 | Changeover minimum output for all controller states. | X | 3 | 142 | Holding | 5132
RC_ChangeOverSelect | 0 | Type of detection to control change-over. | X | 3 | 143 | Holding | 5133
RC_ChangeOverTemperature | 22 | The reference temperature to use in simple mode, in advanced mode the room temperature is used | R | 3 | 144 | Holding | 5134 | 10 | 0
RC_ChangeOverTempHystHeat | 3 | Offset subtracted from the reference temperature when heating. | R | 3 | 147 | Holding | 5135 | 10 | 0
RC_ChangeOverTempHystCool | 4 | Offset added to the reference temperature when cooling. | R | 3 | 150 | Holding | 5136 | 10 | 0
RC_ChangeOverValveTime | 0 | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. | I | 3 | 153 | Holding | 5137
RC_ChangeOverVAVSelect | 0 | Type of detection to control change-over VAV. | X | 3 | 155 | Holding | 5138
RC_ChangeOverVAVTemperature | 22 | The reference temperature to use in simple mode, in advanced mode the room temperature is used | R | 3 | 156 | Holding | 5139 | 10 | 0
RC_ChangeOverVAVTempHystHeat | 3 | Offset added to the reference temperature when switching to heat mode. | R | 3 | 159 | Holding | 5140 | 10 | 0
RC_ChangeOverVAVTempHystCool | 4 | Offset subtracted from the reference temperature when switching to cool mode. | R | 3 | 162 | Holding | 5141 | 10 | 0
RC_ChangeOverVAVValveTime | 0 | The period of time (in seconds) that the valve is open before the pipe medium temperature is measured. | I | 3 | 165 | Holding | 5142
RC_SixWayValveCenterPoint | 5 | Voltage applied to 6 way valve for center point, closed both sequences | R | 3 | 167 | Holding | 5143 | 10 | 0
RC_SixWayValveCenterPointHyst | 2 | Center point Hysteresis | X | 3 | 170 | Holding | 5144
RC_SixWayValveFirstSeqStartOpen | 3.3 | Voltage applied to 6 way valve to start open at sequence 1 | R | 3 | 171 | Holding | 5145 | 10 | 0
RC_SixWayValveFirstSeqFullyOpen | 0 | Voltage applied to 6 way valve for fully open at sequence 1 | R | 3 | 174 | Holding | 5146 | 10 | 0
RC_SixWayValveSecondSeqStartOpen | 6.7 | Voltage applied to 6 way valve to start open at sequence 2 | R | 3 | 177 | Holding | 5147 | 10 | 0
RC_SixWayValveSecondSeqFullyOpen | 10 | Voltage applied to 6 way valve for fully open at sequence 2 | R | 3 | 180 | Holding | 5148 | 10 | 0
RC_SixWayValveSequenceOrder | 1 | Sequence order 0=Cool 1st Sequence 1=Heat 1st Sequence | L | 3 | 183 | Coil | 5012
RC_RoomSetpointHeatOff | 8 | Heating setpoint in Off state (frost protection). | R | 3 | 184 | Holding | 5149 | 10 | 0 | analog_value | 10331 | degrees_celsius | X
RC_RoomSetpointHeatUnoccupied | 15 | Heating setpoint in Unoccupied state. | R | 3 | 187 | Holding | 5150 | 10 | 0 | analog_value | 10341 | degrees_celsius | X
RC_RoomSetpointHeatStandby | 19 | Heating setpoint in Standby state. | R | 3 | 190 | Holding | 5151 | 10 | 0 | analog_value | 10351 | degrees_celsius | X
RC_RoomSetpointHeatOccupied | 22 | Heating setpoint in Occupied state. | R | 3 | 193 | Holding | 5152 | 10 | 0 | analog_value | 10361 | degrees_celsius | X
RC_RoomSetpointCoolUnoccupied | 30 | Cooling setpoint in Unoccupied state. | R | 3 | 196 | Holding | 5153 | 10 | 0 | analog_value | 10371 | degrees_celsius | X
RC_RoomSetpointCoolStandby | 27 | Cooling setpoint in Standby state. | R | 3 | 199 | Holding | 5154 | 10 | 0 | analog_value | 10381 | degrees_celsius | X
RC_RoomSetpointCoolOccupied | 24 | Cooling setpoint in Occupied state. | R | 3 | 202 | Holding | 5155 | 10 | 0 | analog_value | 10391 | degrees_celsius | X
RC_RoomSetpointOffset | 0 | Setpoint offset. Effective in Standby state or higher. | R | 3 | 205 | Holding | 5156 | 10 | 0 | analog_value | 10401 | degrees_celsius | X
RC_RoomSetpointOffsetMaxPos | 3 | Maximum positive setpoint offset. | R | 3 | 208 | Holding | 5157 | 10 | 0 | analog_value | 10411 | degrees_celsius | X
RC_RoomSetpointOffsetMaxNeg | 3 | Maximum negative setpoint offset. | R | 3 | 211 | Holding | 5158 | 10 | 0 | analog_value | 10421 | degrees_celsius | X
RC_RoomPIDPband | 10 | P-band for room PID controller | R | 3 | 214 | Holding | 5159 | 10 | 0 | analog_value | 10431 | degrees_celsius | X
RC_RoomPIDItime | 300 | I-time for room PID controller | R | 3 | 217 | Holding | 5160 | 1 | 0 | analog_value | 10441 | seconds | X
RC_ExtraZoneControlFunction | 0 | Extra Zone function | X | 3 | 220 | Holding | 5161
RC_ExtraZoneSetpoint | 22 | Setpoint for Extra Zone | R | 3 | 221 | Holding | 5162 | 10 | 0 | analog_value | 10451 | degrees_celsius | X
RC_ExtraZoneOutputMax | 100 | Maximum output for Extra Zone | X | 3 | 224 | Holding | 5163
RC_ExtraZoneOutputMin | 0 | Minimum output for Extra Zone | X | 3 | 225 | Holding | 5164
RC_ExtraZonePIDPband | 10 | P-band for Extra Zone PID controller | R | 3 | 226 | Holding | 5165 | 10 | 0 | analog_value | 10461 | degrees_celsius | X
RC_ExtraZonePIDItime | 300 | I-time for Extra Zone PID controller | R | 3 | 229 | Holding | 5166 | 1 | 0 | analog_value | 10471 | seconds | X
RC_ExtraZoneMinControllerState | 0 | Disable Extra Zone control below this controller state | X | 3 | 232 | Holding | 5167
RC_ExtraZoneDisableIfWrongMode | 1 | Disable Extra Zone if mode differs from room PID mode | L | 3 | 233 | Coil | 5013
RC_CO2Setpoint | 600 | Setpoint for CO2 control | R | 3 | 234 | Holding | 5168 | 10 | 0 | analog_value | 10481 | parts_per_million | X
RC_CO2PIDPband | 300 | P-band for CO2 PID controller | R | 3 | 237 | Holding | 5169 | 10 | 0 | analog_value | 10491 | parts_per_million | X
RC_CO2PIDItime | 100 | I-time for CO2 PID controller | R | 3 | 240 | Holding | 5170 | 1 | 0 | analog_value | 10501 | seconds | X
RC_HumiditySetpoint | 70 | Setpoint Humidity control | R | 3 | 243 | Holding | 5171 | 10 | 0 | analog_value | 10511 | percent_relative_humidity | X
RC_HumidityPIDPband | 10 | P-band for Humidity PID controller | R | 3 | 246 | Holding | 5172 | 10 | 0 | analog_value | 10521 | percent_relative_humidity | X
RC_HumidityPIDItime | 300 | I-time for Humidity PID controller | R | 3 | 249 | Holding | 5173 | 1 | 0 | analog_value | 10531 | seconds | X
RC_AirflowSetpoint | 0 | Setpoint for Airflow control | R | 3 | 252 | Holding | 5174 | 10 | 0
RC_AirflowPIDPband | 10 | P-band for Airflow PID controller | R | 3 | 255 | Holding | 5175 | 10 | 0
RC_AirflowPIDItime | 300 | I-time for Airflow PID controller | R | 3 | 258 | Holding | 5176 | 1 | 0
RC_SupplyAirFunction | 2 | Function of supply air limitation | X | 3 | 261 | Holding | 5177
RC_SupplyAirCascadeFactor | 3 | Conversion factor for cascade PI parameters | R | 3 | 262 | Holding | 5178 | 10 | 0 | analog_value | 10541 |  | X
RC_SupplyAirHeatMax | 35 | Max supply air temperature when heating | R | 3 | 265 | Holding | 5179 | 10 | 0 | analog_value | 10551 | degrees_celsius | X
RC_SupplyAirHeatMin | 24 | Min supply air temperature when heating | R | 3 | 268 | Holding | 5180 | 10 | 0 | analog_value | 10561 | degrees_celsius | X
RC_SupplyAirCoolMax | 24 | Max supply air temperature when cooling | R | 3 | 271 | Holding | 5181 | 10 | 0 | analog_value | 10571 | degrees_celsius | X
RC_SupplyAirCoolMin | 12 | Min supply air temperature when cooling | R | 3 | 274 | Holding | 5182 | 10 | 0 | analog_value | 10581 | degrees_celsius | X
RC_SupplyAirFrostProtect | 8 | Min supply air temperature in frost protect | R | 3 | 277 | Holding | 5183 | 10 | 0 | analog_value | 10591 | degrees_celsius | X
RC_FanControlMode | 3 | Select fan control mode | X | 3 | 280 | Holding | 5184
RC_FanSelect | 4 | Fan speed setting | X | 3 | 281 | Holding | 5185 |  |  | multi_state_value | 10031
RC_FanCO2Control | 0 | Fan is controlled by CO2 output | L | 3 | 282 | Coil | 5014
RC_FanHumidityControl | 0 | Fan is controlled by humidity output | L | 3 | 283 | Coil | 5015
RC_FanSpeed1Start | 20 | Output level for fan speed 1 | X | 3 | 284 | Holding | 5186
RC_FanSpeed2Start | 60 | Output level for fan speed 2 | X | 3 | 285 | Holding | 5187
RC_FanSpeed3Start | 100 | Output level for fan speed 3 | X | 3 | 286 | Holding | 5188
RC_FanSpeedMax | 3 | Max fan speed | X | 3 | 287 | Holding | 5189
RC_FanSpeedHyst | 5 | Hysteresis for fan speed outputs | X | 3 | 288 | Holding | 5190
RC_FanSpeedMin | 0 | Fan never stops in auto mode | L | 3 | 289 | Coil | 5016
RC_FanMouldProtect | 0 | Mould protect active. Fan never stops regardless of other settings | L | 3 | 290 | Coil | 5017
RC_FanPreventManualControl | 0 | Prevent manual fan speed setting | L | 3 | 291 | Coil | 5018
RC_FanKickStartTime | 0 | Fan kick start time | X | 3 | 292 | Holding | 5005
RC_FanForcedVentilation | 0 | Fan runs at RC_ECFanSpeedForced when forced ventilation is active | L | 3 | 293 | Coil | 5019
RC_FanBoostMode | 0 | Fan start boost heat cool select. 0=heat, 1=cool, 2=both | X | 3 | 294 | Holding | 5191
RC_FanBoostRunTime | 120 | Fan boost run time. 0 = Not active | I | 3 | 295 | Holding | 5192
RC_FanAfterblowMinSpeed | 0 | Fan afterblow min speed | X | 3 | 297 | Holding | 5193
RC_FanAfterblowTime | 0 | Fan afterblow run time. 0 = Not active | I | 3 | 298 | Holding | 5194
RC_ECFanManualSpeed1 | 20 | EC fan speed for manual speed 1 | X | 3 | 300 | Holding | 5195
RC_ECFanManualSpeed2 | 60 | EC fan speed for manual speed 2 | X | 3 | 301 | Holding | 5196
RC_ECFanManualSpeed3 | 100 | EC fan speed for manual speed 3 | X | 3 | 302 | Holding | 5197
RC_ECFanSpeedForced | 100 | Forced ventilation EC fan speed | X | 3 | 303 | Holding | 5198
RC_ECFanSpeedMax | 100 | Max EC fan speed in % | X | 3 | 304 | Holding | 5199
RC_ECFanSpeedMin | 10 | Min EC fan speed in % | X | 3 | 305 | Holding | 5200
RC_ECFanSpeedStartLimit | 15 | Min EC fan speed in % | X | 3 | 306 | Holding | 5201
RC_ForcedVentMode | 0 | Forced ventilation function | X | 3 | 307 | Holding | 5202
RC_ForcedVentStartLimit | 100 | Forced ventilation start limit | X | 3 | 308 | Holding | 5203
RC_ControllerStateDefault | 3 | The default state when nothing else is controlling the state. | X | 3 | 309 | Holding | 5204 |  |  | multi_state_value | 10041 |  | X
RC_RemoteControllerState | 5 | Sets the state directly via communication. | X | 3 | 310 | Holding | 5205 |  |  | multi_state_value | 10051 |  | X
RC_ControllerStatePresence | 3 | The state to enter when presence is detected. | X | 3 | 311 | Holding | 5206 |  |  | multi_state_value | 10061 |  | X
RC_ControllerStateShutdown | 1 | The state to enter when shutdown mode is set. | X | 3 | 312 | Holding | 5207 |  |  | multi_state_value | 10071 |  | X
RC_ControllerStateFail | 2 | State to set during communication faults | X | 3 | 313 | Holding | 5208 |  |  | multi_state_value | 10081 |  | X
RC_ControllerStateSetBypass | 0 | Set controller in Bypass state | L | 3 | 314 | Coil | 5020
RC_ControllerStateSetShutdown | 0 | Set controller in the state indicated by RC_ControllerStateShutdown | L | 3 | 315 | Coil | 5021
RC_BypassTime | 120 | Bypass time (minutes) | I | 3 | 316 | Holding | 5209 |  |  | analog_value | 10601 | minutes | X
RC_RoomTempRemote | 22 | Remote setting of room temperature | R | 3 | 318 | Holding | 5210 | 10 | 0 | analog_value | 10611 | degrees_celsius | X
RC_CO2LevelRemote | 400 | Remote setting of room CO2 level | R | 3 | 321 | Holding | 5211 | 10 | 0 | analog_value | 10621 | parts_per_million | X
RC_AirFlowRemote | 0 | Remote setting of air flow | R | 3 | 324 | Holding | 5212 | 10 | 0 | analog_value | 10631 | liters_per_second | X
RC_ChangeOverTempRemote | 22 | Remote setting of changeover temperature | R | 3 | 327 | Holding | 5213 | 10 | 0 | analog_value | 10641 | degrees_celsius | X
RC_ChangeOverVAVTempRemote | 22 | Remote setting of changeover VAV temperature | R | 3 | 330 | Holding | 5214 | 10 | 0 | analog_value | 10651 | degrees_celsius | X
RC_ExtraZoneTempRemote | 22 | Remote setting of extra zone temperature | R | 3 | 333 | Holding | 5215 | 10 | 0 | analog_value | 10661 | degrees_celsius | X
RC_SupplyAirTempRemote | 22 | Remote setting of supply air temperature | R | 3 | 336 | Holding | 5216 | 10 | 0 | analog_value | 10671 | degrees_celsius | X
RC_HumidityRemote | 50 | Remote setting of relative humidity | R | 3 | 339 | Holding | 5217 | 10 | 0 | analog_value | 10681 | percent_relative_humidity | X
RC_VOCRemote | 100 | Remote setting of VOC index | R | 3 | 342 | Holding | 5218 | 10 | 0 | analog_value | 10691 |  | X
RC_RoomTempRemoteSelect | 0 | Enable remote setting of room temperature | L | 3 | 345 | Coil | 5022 |  |  | binary_value | 10321 |  | X
RC_CO2LevelRemoteSelect | 0 | Enable remote setting of room CO2 level | L | 3 | 346 | Coil | 5023 |  |  | binary_value | 10331 |  | X
RC_AirFlowRemoteSelect | 0 | Enable remote setting of air flow | L | 3 | 347 | Coil | 5024 |  |  | binary_value | 10341 |  | X
RC_ChangeOverTempRemoteSelect | 0 | Enable remote setting of changeover temperature | L | 3 | 348 | Coil | 5025 |  |  | binary_value | 10351 |  | X
RC_ChangeOverVAVTempRemoteSelect | 0 | Enable remote setting of changeover VAV temperature | L | 3 | 349 | Coil | 5026 |  |  | binary_value | 10361 |  | X
RC_ExtraZoneTempRemoteSelect | 0 | Enable remote setting of extra zone temperature | L | 3 | 350 | Coil | 5027 |  |  | binary_value | 10371 |  | X
RC_SupplyAirTempRemoteSelect | 0 | Enable remote setting of supply air temperature | L | 3 | 351 | Coil | 5028 |  |  | binary_value | 10381 |  | X
RC_HumidityRemoteSelect | 0 | Enable remote setting of relative humidity | L | 3 | 352 | Coil | 5029 |  |  | binary_value | 10391 |  | X
RC_VOCRemoteSelect | 0 | Enable remote setting of VOC index | L | 3 | 353 | Coil | 5030 |  |  | binary_value | 10401 |  | X
RC_DIPresenceRemote | 0 | Remote setting of presence digital input | L | 3 | 354 | Coil | 5031 |  |  | binary_value | 10411 |  | X
RC_DIOpenWindowRemote | 0 | Remote setting of window contact digital input | L | 3 | 355 | Coil | 5032 |  |  | binary_value | 10421 |  | X
RC_DIChangeoverRemote | 0 | Remote setting of change over digital input | L | 3 | 356 | Coil | 5033 |  |  | binary_value | 10431 |  | X
RC_DIChangeoverVAVRemote | 0 | Remote setting of change over VAV digital input | L | 3 | 357 | Coil | 5034 |  |  | binary_value | 10441 |  | X
RC_DICondensationRemote | 0 | Remote setting of condensation digital input | L | 3 | 358 | Coil | 5035 |  |  | binary_value | 10451 |  | X
RC_RoomHeat1OutputManual | 0 | Manual setting of RoomHeat1Output | X | 3 | 359 | Holding | 5219 |  |  | analog_value | 10701 | percent | X
RC_RoomCool1OutputManual | 0 | Manual setting of RoomCool1Output | X | 3 | 360 | Holding | 5220 |  |  | analog_value | 10711 | percent | X
RC_RoomVAV1OutputManual | 0 | Manual setting of RoomVAV1Output | X | 3 | 361 | Holding | 5221 |  |  | analog_value | 10721 | percent | X
RC_RoomHeat2OutputManual | 0 | Manual setting of RoomHeat2Output | X | 3 | 362 | Holding | 5222 |  |  | analog_value | 10731 | percent | X
RC_RoomCool2OutputManual | 0 | Manual setting of RoomCool2Output | X | 3 | 363 | Holding | 5223 |  |  | analog_value | 10741 | percent | X
RC_RoomVAV2OutputManual | 0 | Manual setting of RoomVAV2Output | X | 3 | 364 | Holding | 5224 |  |  | analog_value | 10751 | percent | X
RC_RoomChangeOverOutputManual | 0 | Manual setting of RoomChangeOverOutput | X | 3 | 365 | Holding | 5225 |  |  | analog_value | 10761 | percent | X
RC_Room6WayValveOutputManual | 0 | Manual setting of Room6WayValveOutput | X | 3 | 366 | Holding | 5226 |  |  | analog_value | 10771 | percent | X
RC_RoomChangeOverVAVOutputManual | 0 | Manual setting of RoomChangeOverVAVOutput | X | 3 | 367 | Holding | 5227 |  |  | analog_value | 10781 | percent | X
RC_ExtraZoneOutputManual | 0 | Manual setting of ExtraZoneOutput | X | 3 | 368 | Holding | 5228 |  |  | analog_value | 10791 | percent | X
RC_ECFanSpeedManual | 0 | Manual setting of ECFanSpeed | X | 3 | 369 | Holding | 5229 |  |  | analog_value | 10801 |  | X
RC_CO2ControlManual | 0 | Manual setting of CO2Control | X | 3 | 370 | Holding | 5230 |  |  | analog_value | 10811 | percent | X
RC_HumidifyOutputManual | 0 | Manual setting of HumidifyOutput | X | 3 | 371 | Holding | 5231 |  |  | analog_value | 10821 |  | X
RC_DehumidifyOutputManual | 0 | Manual setting of DehumidifyOutput | X | 3 | 372 | Holding | 5232 |  |  | analog_value | 10831 | percent | X
RC_AirflowControlManual | 0 | Manual setting of AirflowControl | X | 3 | 373 | Holding | 5233
RC_RoomHeat1OutputManSelect | 2 | Manual/auto select for RoomHeat1Output | X | 3 | 374 | Holding | 5234 |  |  | multi_state_value | 10091 |  | X
RC_RoomCool1OutputManSelect | 2 | Manual/auto select for RoomCool1Output | X | 3 | 375 | Holding | 5235 |  |  | multi_state_value | 10101 |  | X
RC_RoomVAV1OutputManSelect | 2 | Manual/auto select for RoomVAV1Output | X | 3 | 376 | Holding | 5236 |  |  | multi_state_value | 10111 |  | X
RC_RoomHeat2OutputManSelect | 2 | Manual/auto select for RoomHeat2Output | X | 3 | 377 | Holding | 5237 |  |  | multi_state_value | 10121 |  | X
RC_RoomCool2OutputManSelect | 2 | Manual/auto select for RoomCool2Output | X | 3 | 378 | Holding | 5238 |  |  | multi_state_value | 10131 |  | X
RC_RoomVAV2OutputManSelect | 2 | Manual/auto select for RoomVAV2Output | X | 3 | 379 | Holding | 5239 |  |  | multi_state_value | 10141 |  | X
RC_RoomChangeOverOutputManSelect | 2 | Manual/auto select for RoomChangeOverOutput | X | 3 | 380 | Holding | 5240
RC_Room6WayValveOutputManSelect | 2 | Manual/auto select for Room6WayValveOutput | X | 3 | 381 | Holding | 5241 |  |  | multi_state_value | 10151 |  | X
RC_RoomChangeOverVAVOutputManSelect | 2 | Manual/auto select for RoomChangeOverVAVOutput | X | 3 | 382 | Holding | 5242 |  |  | multi_state_value | 10161 |  | X
RC_ExtraZoneOutputManSelect | 2 | Manual/auto select for ExtraZoneOutput | X | 3 | 383 | Holding | 5243 |  |  | multi_state_value | 10171 |  | X
RC_ECFanSpeedManSelect | 2 | Manual/auto select for ECFanSpeed | X | 3 | 384 | Holding | 5244 |  |  | multi_state_value | 10181 |  | X
RC_CO2ControlManSelect | 2 | Manual/auto select for CO2Control | X | 3 | 385 | Holding | 5245 |  |  | multi_state_value | 10191 |  | X
RC_HumidifyOutputManSelect | 2 | Manual/auto select for HumidifyOutput | X | 3 | 386 | Holding | 5246 |  |  | multi_state_value | 10201 |  | X
RC_DehumidifyOutputManSelect | 2 | Manual/auto select for DehumidifyOutput | X | 3 | 387 | Holding | 5247 |  |  | multi_state_value | 10211 |  | X
RC_AirflowControlManSelect | 2 | Manual/auto select for AirflowControl | X | 3 | 388 | Holding | 5248
RC_PresenceDelayOn | 0 | Delay for presence on (min) | I | 3 | 389 | Holding | 5249
RC_PresenceDelayOff | 10 | Delay for presence off (min) | I | 3 | 391 | Holding | 5250
RC_PresenceCO2Enable | 0 | Enable CO2 presence detection | L | 3 | 393 | Coil | 5036
RC_PresenceCO2Limit | 800 | CO2 presence limit | R | 3 | 394 | Holding | 5251 | 10 | 0
RC_PresenceCO2Hyst | 160 | CO2 presence limit hysteresis | R | 3 | 397 | Holding | 5252 | 10 | 0
RC_ValveExerciseFunction | 0 | Valve exercise function | X | 3 | 400 | Holding | 5253
RC_ValveExerciseIntervalHeat1 | 23 | Heat valve 1 exercise interval (hours) | X | 3 | 401 | Holding | 5254
RC_ValveExerciseIntervalCool1 | 23 | Cool valve 1 exercise interval (hours) | X | 3 | 402 | Holding | 5255
RC_ValveExerciseIntervalHeat2 | 23 | Heat valve 2 exercise interval (hours) | X | 3 | 403 | Holding | 5256
RC_ValveExerciseIntervalCool2 | 23 | Cool valve 2 exercise interval (hours) | X | 3 | 404 | Holding | 5257
RC_ValveExerciseIntervalChangeOver | 23 | Change-over valve exercise interval (hours) | X | 3 | 405 | Holding | 5258
RC_ValveExerciseInterval6Way | 23 | 6-way valve exercise interval (hours) | X | 3 | 406 | Holding | 5259
RC_ValveRuntimeHeat1 | 120 | Heat valve 1 runtime (seconds) | I | 3 | 407 | Holding | 5260
RC_ValveRuntimeCool1 | 120 | Cool valve 1 runtime (seconds) | I | 3 | 409 | Holding | 5261
RC_ValveRuntimeHeat2 | 120 | Heat valve 2 runtime (seconds) | I | 3 | 411 | Holding | 5262
RC_ValveRuntimeCool2 | 120 | Cool valve 2 runtime (seconds) | I | 3 | 413 | Holding | 5263
RC_ValveRuntimeChangeOver | 120 | Change-over valve runtime (seconds) | I | 3 | 415 | Holding | 5264
RC_ValveRuntime6Way | 120 | 6-way valve runtime (seconds) | I | 3 | 417 | Holding | 5265
RC_AlarmRoomTempLimitHigh | 40 | High room temp alarm limit | R | 3 | 419 | Holding | 5266 | 10 | 0 | analog_value | 10841 | degrees_celsius | X
RC_AlarmRoomTempLimitLow | 15 | Low room temp alarm limit | R | 3 | 422 | Holding | 5267 | 10 | 0 | analog_value | 10851 | degrees_celsius | X
RC_AlarmCO2LimitHigh | 2000 | High CO2 alarm limit | R | 3 | 425 | Holding | 5268 | 10 | 0 | analog_value | 10861 | parts_per_million | X
RC_ResetUserSettingsAtShutdown | 0 | Reset user settings in shutdown state | L | 3 | 428 | Coil | 5037
RC_DamperPositionRemote | 0 | Remote setting of damper position | R | 3 | 429 | Holding | 5269 | 10 | 0 | analog_value | 10871 |  | X
RC_ExtractTemperaureRemote | 22 | Remote setting of extract temperature | R | 3 | 432 | Holding | 5270 | 10 | 0 | analog_value | 10881 | degrees_celsius | X
RC_DamperPositionRemoteSelect | 0 | Enable remote setting of damper position | L | 3 | 435 | Coil | 5038 |  |  | binary_value | 10461 |  | X
RC_ExtractTemperaureRemoteSelect | 0 | Enable remote setting of extract temperature | L | 3 | 436 | Coil | 5039 |  |  | binary_value | 10471 |  | X
RC_DIPresenceRemoteSelect | 0 | Enable remote setting of presence digital input | L | 3 | 437 | Coil | 5040 |  |  | binary_value | 10481 |  | X
RC_DIOpenWindowRemoteSelect | 0 | Enable remote setting of window contact digital input | L | 3 | 438 | Coil | 5041 |  |  | binary_value | 10491 |  | X
RC_DIChangeoverRemoteSelect | 0 | Enable remote setting of change over digital input | L | 3 | 439 | Coil | 5042 |  |  | binary_value | 10501 |  | X
RC_DIChangeoverVAVRemoteSelect | 0 | Enable remote setting of change over VAV digital input | L | 3 | 440 | Coil | 5043 |  |  | binary_value | 10511 |  | X
RC_DICondensationRemoteSelect | 0 | Enable remote setting of condensation digital input | L | 3 | 441 | Coil | 5044 |  |  | binary_value | 10521 |  | X
RC_DisplayViewMode | 0 | Select value to be shown in the display | X | 3 | 442 | Holding | 5271 |  |  | multi_state_value | 10221 |  | X
RC_DisplaySetpointMode | 0 | Select setpoint display at setpoint adjustment | X | 3 | 443 | Holding | 5272 |  |  | multi_state_value | 10231 |  | X
RC_RoomHeat1OutputManSelectDO | 2 | Manual/auto select Heat1 output digital | X | 3 | 444 | Holding | 5273 |  |  | multi_state_value | 10241 |  | X
RC_RoomCool1OutputManSelectDO | 2 | Manual/auto select Cool1 output digital | X | 3 | 445 | Holding | 5274 |  |  | multi_state_value | 10251 |  | X
RC_RoomVAV1OutputManSelectDO | 2 | Manual/auto select VAV1 output digital | X | 3 | 446 | Holding | 5275 |  |  | multi_state_value | 10261 |  | X
RC_RoomHeat2OutputManSelectDO | 2 | Manual/auto select Heat2 output digital | X | 3 | 447 | Holding | 5276 |  |  | multi_state_value | 10271 |  | X
RC_RoomCool2OutputManSelectDO | 2 | Manual/auto select Cool2 output digital | X | 3 | 448 | Holding | 5277 |  |  | multi_state_value | 10281 |  | X
RC_RoomVAV2OutputManSelectDO | 2 | Manual/auto select VAV2 output digital | X | 3 | 449 | Holding | 5278 |  |  | multi_state_value | 10291 |  | X
RC_RoomChangeOverOutputManSelectDO | 2 | Manual/auto select Change over output digital | X | 3 | 450 | Holding | 5279 |  |  | multi_state_value | 10301 |  | X
RC_Room6WayValveOutputManSelectDO | 2 | Manual/auto select 6-way valve output digital | X | 3 | 451 | Holding | 5280 |  |  | multi_state_value | 10311 |  | X
RC_RoomChangeOverVAVOutputManSelectDO | 2 | Manual/auto select Change over VAV output digital | X | 3 | 452 | Holding | 5281 |  |  | multi_state_value | 10321 |  | X
RC_ExtraZoneOutputManSelectDO | 2 | Manual/auto select Extra Zone output digital | X | 3 | 453 | Holding | 5282 |  |  | multi_state_value | 10331 |  | X
RC_CO2ControlManSelectDO | 2 | Manual/auto select CO2 control digital out | X | 3 | 454 | Holding | 5283 |  |  | multi_state_value | 10341 |  | X
RC_HumidifyOutputManSelectDO | 2 | Manual/auto select Humidify digital out | X | 3 | 455 | Holding | 5284 |  |  | multi_state_value | 10351 |  | X
RC_DehumidifyOutputManSelectDO | 2 | Manual/auto select Dehumidify digital out | X | 3 | 456 | Holding | 5285 |  |  | multi_state_value | 10361 |  | X
RC_AirflowControlManSelectDO | 2 | Manual/auto select Airflow control digital out | X | 3 | 457 | Holding | 5286
RC_ForcedVentilationManSelectDO | 2 | Manual/auto select Forced Ventilation digital out | X | 3 | 458 | Holding | 5287 |  |  | multi_state_value | 10371 |  | X
RC_LightControlManSelectDO | 2 | Manual/auto select Light control digital out | X | 3 | 459 | Holding | 5288
RC_SumAlarmManSelectDO | 2 | Manual/auto select Sum Alarm | X | 3 | 460 | Holding | 5289 |  |  | multi_state_value | 10381 |  | X
RC_ExtraZoneActiveManSelectDO | 2 | Manual/auto select Extra Zone active digital out | X | 3 | 461 | Holding | 5290 |  |  | multi_state_value | 10391 |  | X
RC_CO2_0V | 0 | CO2 at 0 Volt input | R | 3 | 462 | Holding | 5291 | 1 | 0
RC_CO2_10V | 2000 | CO2 at 10 Volt input | R | 3 | 465 | Holding | 5292 | 1 | 0
RC_RH_0V | 0 | RH at 0 Volt input | R | 3 | 468 | Holding | 5293 | 10 | 0
RC_RH_10V | 100 | RH at 10 Volt input | R | 3 | 471 | Holding | 5294 | 10 | 0
RC_RoomTemp_0V | 0 | Room temperature at 0 Volt input | R | 3 | 474 | Holding | 5295 | 10 | 0
RC_RoomTemp_10V | 100 | Room temperature at 10 Volt input | R | 3 | 477 | Holding | 5296 | 10 | 0
RC_Flow_0V | 0 | Air flow at 0 Volt input | R | 3 | 480 | Holding | 5297 | 10 | 0
RC_Flow_10V | 100 | Air flow at 10 Volt input | R | 3 | 483 | Holding | 5298 | 10 | 0
RC_VOC_0V | 0 | VOC index at 0 Volt input | R | 3 | 486 | Holding | 5299 | 10 | 0
RC_VOC_10V | 500 | VOC index at 10 Volt input | R | 3 | 489 | Holding | 5300 | 10 | 0
RC_CO2FilterTime | 5 | CO2 filter time (0 to 17200 seconds) | I | 3 | 492 | Holding | 5301
RC_RHFilterTime | 5 | RH filter time (0 to 17200 seconds) | I | 3 | 494 | Holding | 5302
RC_TempFilterTime | 5 | Temperature filter time (0 to 17200 seconds) | I | 3 | 496 | Holding | 5303
RC_FlowFilterTime | 5 | Air flow filter time (0 to 17200 seconds) | I | 3 | 498 | Holding | 5304
RC_VOCFilterTime | 5 | VOC index filter time (0 to 17200 seconds) | I | 3 | 500 | Holding | 5305
RC_CO2LevelYellow | 800 | CO2 level for yellow led | R | 3 | 502 | Holding | 5306 | 1 | 0 | analog_value | 10891 | parts_per_million | X
RC_CO2LevelRed | 1000 | CO2 level for red led | R | 3 | 505 | Holding | 5307 | 1 | 0 | analog_value | 10901 | parts_per_million | X
RC_CO2SetIndication | 0 | Enable/disable CO2 led indication | X | 3 | 508 | Holding | 5308
RC_FanBoostShortTime | 10 | Fan boost short run time | I | 3 | 509 | Holding | 5309
RC_FanBoostPBand | 5 | Fan boost P band | R | 3 | 511 | Holding | 5310 | 1 | 0
RC_CO2Step | 1 | Min step for CO2 value | R | 3 | 514 | Holding | 5311 | 1 | 0
RC_TemperatureCO2 | 0 | Alternate temperaure/CO2 display | L | 3 | 517 | Coil | 5045
RC_ForcedApplicationOff | 0 | Set to 1 to disable all regulator functions | L | 3 | 518 | Coil | 5046
RC_VOCSetpoint | 100 | Setpoint for VOC control | R | 3 | 519 | Holding | 5312 | 10 | 0 | analog_value | 10911 | no_units | X
RC_VOCPIDPband | 50 | P-band for VOC PID controller | R | 3 | 522 | Holding | 5313 | 10 | 0 | analog_value | 10921 | no_units | X
RC_VOCPIDItime | 300 | I-time for VOC PID controller | R | 3 | 525 | Holding | 5314 | 1 | 0 | analog_value | 10931 | seconds | X
RC_VOCControlManual | 0 | Manual setting of VOCControl | X | 3 | 528 | Holding | 5315 |  |  | analog_value | 10941 | percent | X
RC_VOCControlManSelect | 2 | Manual/auto select for VOCControl | X | 3 | 529 | Holding | 5316 |  |  | multi_state_value | 10401 |  | X
RC_VOCControlManSelectDO | 2 | Manual/auto select VOC control digital out | X | 3 | 530 | Holding | 5317 |  |  | multi_state_value | 10411 |  | X
RC_ControllerStateWindow | 0 | The state to enter when the window is opened | X | 3 | 531 | Holding | 5318 |  |  | multi_state_value | 10421 |  | X
RC_DIAlarmRemote | 0 | Remote setting of alarm digital input | L | 3 | 532 | Coil | 5047
RC_DIAlarmRemoteSelect | 0 | Enable remote setting of alarm digital input | L | 3 | 533 | Coil | 5048
RC_VAV2OutputMaxHeat | 0 | VAV2 maximum output when the controller is in heating mode. | X | 3 | 534 | Holding | 5319
RC_PIDPresence | 1 | Use internal PID sensor for presence detection | L | 3 | 535 | Coil | 5049
RC_RoomTempHeatHyst | 2 | Room temperature heating hysteresis for thermostat | R | 3 | 536 | Holding | 5320 | 10 | 0
RC_RoomTempCoolHyst | 2 | Room temperature cooling hysteresis for thermostat | R | 3 | 539 | Holding | 5321 | 10 | 0
RC_ExtraZoneTempHyst | 2 | Extra zone temperature hysteresis for thermostat | R | 3 | 542 | Holding | 5322 | 10 | 0
RC_Flow_unit | 95 | BACnet unit for air flow | I | 3 | 545 | Holding | 5323
RC_Room6WayValveOutputHeatCool | 0 | Manual setting of 6-way valve heat/cool | L | 3 | 547 | Coil | 5050
RC_VAVControlHumidity | 0 | VAV controlled by humidify or dehumidify output | X | 3 | 548 | Holding | 5324
RC_VAVControlVOC | 0 | VAV is controlled by VOC output | L | 3 | 549 | Coil | 5051
IoAnaIn_1_value |  | Filtered value from sensor | R | 4 | 0 | Input | 1001 | 100 | 0 | analog_value | 1001
IoAnaIn_1_mode | 3 | Mode for input | X | 4 | 3 | Holding | 1001
IoAnaIn_1_unit | 0 | Unit converter | X | 4 | 4 | Holding | 1002
IoAnaIn_1_min_in | -100 | Scale for input | R | 4 | 5 | Holding | 1003 | 100 | 0
IoAnaIn_1_min_out | -100 | Scale for input | R | 4 | 8 | Holding | 1005 | 100 | 0
IoAnaIn_1_max_in | 10000 | Scale for input | R | 4 | 11 | Holding | 1007 | 100 | 0
IoAnaIn_1_max_out | 10000 | Scale for input | R | 4 | 14 | Holding | 1009 | 100 | 0
IoAnaIn_1_prefilter |  | Unfiltered value from sensor | R | 4 | 23 | Input | 1003 | 100 | 0
IoAnaIn_1_raw |  | Raw value from sensor | R | 4 | 26 | Input | 1005 | 100 | 0
IoAnaIn_1_override | 0 | Override value | R | 4 | 29 | Holding | 1014 | 100 | 0 | analog_value | 1101 |  | X
IoAnaIn_1_override_en | 0 | Set to 1 to enable override | L | 4 | 32 | Coil | 1001 |  |  | binary_value | 1001 |  | X
IoAnaIn_1_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 37 | Holding | 1018
IoAnaIn_1_hyst | 0 | Hysteresis limit | R | 4 | 40 | Holding | 1019 | 100 | 0
IoAnaIn_1_accumulate | 100 | Time in milli seconds to accumulate samples before processing | I | 4 | 43 | Holding | 1020
IoAnaIn_1_valueDigits | 2 | Number of shown digits | I | 4 | 46 | Holding | 1021
IoAnaIn_2_value |  | Filtered value from sensor | R | 4 | 50 | Input | 1026 | 100 | 0 | analog_value | 1002
IoAnaIn_2_mode | 9 | Mode for input | X | 4 | 53 | Holding | 1026
IoAnaIn_2_unit | 0 | Unit converter | X | 4 | 54 | Holding | 1027
IoAnaIn_2_min_in | -100 | Scale for input | R | 4 | 55 | Holding | 1028 | 100 | 0
IoAnaIn_2_min_out | -100 | Scale for input | R | 4 | 58 | Holding | 1030 | 100 | 0
IoAnaIn_2_max_in | 10000 | Scale for input | R | 4 | 61 | Holding | 1032 | 100 | 0
IoAnaIn_2_max_out | 10000 | Scale for input | R | 4 | 64 | Holding | 1034 | 100 | 0
IoAnaIn_2_prefilter |  | Unfiltered value from sensor | R | 4 | 73 | Input | 1028 | 100 | 0
IoAnaIn_2_raw |  | Raw value from sensor | R | 4 | 76 | Input | 1030 | 100 | 0
IoAnaIn_2_override | 0 | Override value | R | 4 | 79 | Holding | 1039 | 100 | 0 | analog_value | 1102 |  | X
IoAnaIn_2_override_en | 0 | Set to 1 to enable override | L | 4 | 82 | Coil | 1026 |  |  | binary_value | 1002 |  | X
IoAnaIn_2_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 87 | Holding | 1043
IoAnaIn_2_hyst | 0 | Hysteresis limit | R | 4 | 90 | Holding | 1044 | 100 | 0
IoAnaIn_2_accumulate | 100 | Time in milli seconds to accumulate samples before processing | I | 4 | 93 | Holding | 1045
IoAnaIn_2_valueDigits | 2 | Number of shown digits | I | 4 | 96 | Holding | 1046
IoAnaIn_3_value |  | Filtered value from sensor | R | 4 | 100 | Input | 1051 | 100 | 0 | analog_value | 1003
IoAnaIn_3_mode | 9 | Mode for input | X | 4 | 103 | Holding | 1051
IoAnaIn_3_unit | 0 | Unit converter | X | 4 | 104 | Holding | 1052
IoAnaIn_3_min_in | -100 | Scale for input | R | 4 | 105 | Holding | 1053 | 100 | 0
IoAnaIn_3_min_out | -100 | Scale for input | R | 4 | 108 | Holding | 1055 | 100 | 0
IoAnaIn_3_max_in | 10000 | Scale for input | R | 4 | 111 | Holding | 1057 | 100 | 0
IoAnaIn_3_max_out | 10000 | Scale for input | R | 4 | 114 | Holding | 1059 | 100 | 0
IoAnaIn_3_prefilter |  | Unfiltered value from sensor | R | 4 | 123 | Input | 1053 | 100 | 0
IoAnaIn_3_raw |  | Raw value from sensor | R | 4 | 126 | Input | 1055 | 100 | 0
IoAnaIn_3_override | 0 | Override value | R | 4 | 129 | Holding | 1064 | 100 | 0 | analog_value | 1103 |  | X
IoAnaIn_3_override_en | 0 | Set to 1 to enable override | L | 4 | 132 | Coil | 1051 |  |  | binary_value | 1003 |  | X
IoAnaIn_3_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 137 | Holding | 1068
IoAnaIn_3_hyst | 0 | Hysteresis limit | R | 4 | 140 | Holding | 1069 | 100 | 0
IoAnaIn_3_accumulate | 100 | Time in milli seconds to accumulate samples before processing | I | 4 | 143 | Holding | 1070
IoAnaIn_4_value |  | Filtered value from sensor | R | 4 | 150 | Input | 1076 | 100 | 0 | analog_value | 1004
IoAnaIn_4_mode | 135 | Mode for input | X | 4 | 153 | Holding | 1076
IoAnaIn_4_unit | 0 | Unit converter | X | 4 | 154 | Holding | 1077
IoAnaIn_4_min_in | -100 | Scale for input | R | 4 | 155 | Holding | 1078 | 100 | 0
IoAnaIn_4_min_out | -100 | Scale for input | R | 4 | 158 | Holding | 1080 | 100 | 0
IoAnaIn_4_max_in | 10000 | Scale for input | R | 4 | 161 | Holding | 1082 | 100 | 0
IoAnaIn_4_max_out | 10000 | Scale for input | R | 4 | 164 | Holding | 1084 | 100 | 0
IoAnaIn_4_prefilter |  | Unfiltered value from sensor | R | 4 | 173 | Input | 1078 | 100 | 0
IoAnaIn_4_raw |  | Raw value from sensor | R | 4 | 176 | Input | 1080 | 100 | 0
IoAnaIn_4_override | 0 | Override value | R | 4 | 179 | Holding | 1089 | 100 | 0 | analog_value | 1104 |  | X
IoAnaIn_4_override_en | 0 | Set to 1 to enable override | L | 4 | 182 | Coil | 1076 |  |  | binary_value | 1004 |  | X
IoAnaIn_4_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 187 | Holding | 1093
IoAnaIn_4_hyst | 0 | Hysteresis limit | R | 4 | 190 | Holding | 1094 | 100 | 0
IoAnaIn_4_accumulate | 100 | Time in milli seconds to accumulate samples before processing | I | 4 | 193 | Holding | 1095
IoAnaIn_5_value |  | Filtered value from sensor | R | 4 | 200 | Input | 1101 | 100 | 0 | analog_value | 1005
IoAnaIn_5_mode | 128 | Mode for input | X | 4 | 203 | Holding | 1101
IoAnaIn_5_unit | 0 | Unit converter | X | 4 | 204 | Holding | 1102
IoAnaIn_5_min_in | -100 | Scale for input | R | 4 | 205 | Holding | 1103 | 100 | 0
IoAnaIn_5_min_out | -100 | Scale for input | R | 4 | 208 | Holding | 1105 | 100 | 0
IoAnaIn_5_max_in | 10000 | Scale for input | R | 4 | 211 | Holding | 1107 | 100 | 0
IoAnaIn_5_max_out | 10000 | Scale for input | R | 4 | 214 | Holding | 1109 | 100 | 0
IoAnaIn_5_prefilter |  | Unfiltered value from sensor | R | 4 | 223 | Input | 1103 | 100 | 0
IoAnaIn_5_raw |  | Raw value from sensor | R | 4 | 226 | Input | 1105 | 100 | 0
IoAnaIn_5_override | 0 | Override value | R | 4 | 229 | Holding | 1114 | 100 | 0 | analog_value | 1105 |  | X
IoAnaIn_5_override_en | 0 | Set to 1 to enable override | L | 4 | 232 | Coil | 1101 |  |  | binary_value | 1005 |  | X
IoAnaIn_5_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 237 | Holding | 1118
IoAnaIn_5_hyst | 0 | Hysteresis limit | R | 4 | 240 | Holding | 1119 | 100 | 0
IoAnaIn_6_value |  | Filtered value from sensor | R | 4 | 250 | Input | 1126 | 100 | 0 | analog_value | 1006
IoAnaIn_6_mode | 128 | Mode for input | X | 4 | 253 | Holding | 1126
IoAnaIn_6_unit | 0 | Unit converter | X | 4 | 254 | Holding | 1127
IoAnaIn_6_min_in | -100 | Scale for input | R | 4 | 255 | Holding | 1128 | 100 | 0
IoAnaIn_6_min_out | -100 | Scale for input | R | 4 | 258 | Holding | 1130 | 100 | 0
IoAnaIn_6_max_in | 10000 | Scale for input | R | 4 | 261 | Holding | 1132 | 100 | 0
IoAnaIn_6_max_out | 10000 | Scale for input | R | 4 | 264 | Holding | 1134 | 100 | 0
IoAnaIn_6_prefilter |  | Unfiltered value from sensor | R | 4 | 273 | Input | 1128 | 100 | 0
IoAnaIn_6_raw |  | Raw value from sensor | R | 4 | 276 | Input | 1130 | 100 | 0
IoAnaIn_6_override | 0 | Override value | R | 4 | 279 | Holding | 1139 | 100 | 0 | analog_value | 1106 |  | X
IoAnaIn_6_override_en | 0 | Set to 1 to enable override | L | 4 | 282 | Coil | 1126 |  |  | binary_value | 1006 |  | X
IoAnaIn_6_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 287 | Holding | 1143
IoAnaIn_6_hyst | 0 | Hysteresis limit | R | 4 | 290 | Holding | 1144 | 100 | 0
IoAnaIn_7_value |  | Filtered value from sensor | R | 4 | 300 | Input | 1151 | 100 | 0 | analog_value | 1007
IoAnaIn_7_mode | 128 | Mode for input | X | 4 | 303 | Holding | 1151
IoAnaIn_7_unit | 0 | Unit converter | X | 4 | 304 | Holding | 1152
IoAnaIn_7_min_in | -100 | Scale for input | R | 4 | 305 | Holding | 1153 | 100 | 0
IoAnaIn_7_min_out | -100 | Scale for input | R | 4 | 308 | Holding | 1155 | 100 | 0
IoAnaIn_7_max_in | 10000 | Scale for input | R | 4 | 311 | Holding | 1157 | 100 | 0
IoAnaIn_7_max_out | 10000 | Scale for input | R | 4 | 314 | Holding | 1159 | 100 | 0
IoAnaIn_7_prefilter |  | Unfiltered value from sensor | R | 4 | 323 | Input | 1153 | 100 | 0
IoAnaIn_7_raw |  | Raw value from sensor | R | 4 | 326 | Input | 1155 | 100 | 0
IoAnaIn_7_override | 0 | Override value | R | 4 | 329 | Holding | 1164 | 100 | 0 | analog_value | 1107 |  | X
IoAnaIn_7_override_en | 0 | Set to 1 to enable override | L | 4 | 332 | Coil | 1151 |  |  | binary_value | 1007 |  | X
IoAnaIn_7_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 337 | Holding | 1168
IoAnaIn_7_hyst | 0 | Hysteresis limit | R | 4 | 340 | Holding | 1169 | 100 | 0
IoAnaIn_8_value |  | Filtered value from sensor | R | 4 | 350 | Input | 1176 | 100 | 0 | analog_value | 1008
IoAnaIn_8_mode | 128 | Mode for input | X | 4 | 353 | Holding | 1176
IoAnaIn_8_unit | 0 | Unit converter | X | 4 | 354 | Holding | 1177
IoAnaIn_8_min_in | -100 | Scale for input | R | 4 | 355 | Holding | 1178 | 100 | 0
IoAnaIn_8_min_out | -100 | Scale for input | R | 4 | 358 | Holding | 1180 | 100 | 0
IoAnaIn_8_max_in | 10000 | Scale for input | R | 4 | 361 | Holding | 1182 | 100 | 0
IoAnaIn_8_max_out | 10000 | Scale for input | R | 4 | 364 | Holding | 1184 | 100 | 0
IoAnaIn_8_prefilter |  | Unfiltered value from sensor | R | 4 | 373 | Input | 1178 | 100 | 0
IoAnaIn_8_raw |  | Raw value from sensor | R | 4 | 376 | Input | 1180 | 100 | 0
IoAnaIn_8_override | 0 | Override value | R | 4 | 379 | Holding | 1189 | 100 | 0 | analog_value | 1108 |  | X
IoAnaIn_8_override_en | 0 | Set to 1 to enable override | L | 4 | 382 | Coil | 1176 |  |  | binary_value | 1008 |  | X
IoAnaIn_8_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 387 | Holding | 1193
IoAnaIn_8_hyst | 0 | Hysteresis limit | R | 4 | 390 | Holding | 1194 | 100 | 0
IoAnaIn_8_valueDigits | 2 | Number of shown digits | I | 4 | 396 | Holding | 1196
IoAnaIn_9_value |  | Filtered value from sensor | R | 4 | 400 | Input | 1201 | 100 | 0 | analog_value | 1009
IoAnaIn_9_mode | 9 | Mode for input | X | 4 | 403 | Holding | 1201
IoAnaIn_9_unit | 0 | Unit converter | X | 4 | 404 | Holding | 1202
IoAnaIn_9_min_in | -100 | Scale for input | R | 4 | 405 | Holding | 1203 | 100 | 0
IoAnaIn_9_min_out | -100 | Scale for input | R | 4 | 408 | Holding | 1205 | 100 | 0
IoAnaIn_9_max_in | 10000 | Scale for input | R | 4 | 411 | Holding | 1207 | 100 | 0
IoAnaIn_9_max_out | 10000 | Scale for input | R | 4 | 414 | Holding | 1209 | 100 | 0
IoAnaIn_9_prefilter |  | Unfiltered value from sensor | R | 4 | 423 | Input | 1203 | 100 | 0
IoAnaIn_9_raw |  | Raw value from sensor | R | 4 | 426 | Input | 1205 | 100 | 0
IoAnaIn_9_override | 0 | Override value | R | 4 | 429 | Holding | 1214 | 100 | 0 | analog_value | 1109 |  | X
IoAnaIn_9_override_en | 0 | Set to 1 to enable override | L | 4 | 432 | Coil | 1201 |  |  | binary_value | 1009 |  | X
IoAnaIn_9_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 437 | Holding | 1218
IoAnaIn_9_hyst | 0 | Hysteresis limit | R | 4 | 440 | Holding | 1219 | 100 | 0
IoAnaIn_10_value |  | Filtered value from sensor | R | 4 | 450 | Input | 1226 | 100 | 0 | analog_value | 1010
IoAnaIn_10_mode | 128 | Mode for input | X | 4 | 453 | Holding | 1226
IoAnaIn_10_unit | 0 | Unit converter | X | 4 | 454 | Holding | 1227
IoAnaIn_10_min_in | -100 | Scale for input | R | 4 | 455 | Holding | 1228 | 100 | 0
IoAnaIn_10_min_out | -100 | Scale for input | R | 4 | 458 | Holding | 1230 | 100 | 0
IoAnaIn_10_max_in | 10000 | Scale for input | R | 4 | 461 | Holding | 1232 | 100 | 0
IoAnaIn_10_max_out | 10000 | Scale for input | R | 4 | 464 | Holding | 1234 | 100 | 0
IoAnaIn_10_prefilter |  | Unfiltered value from sensor | R | 4 | 473 | Input | 1228 | 100 | 0
IoAnaIn_10_raw |  | Raw value from sensor | R | 4 | 476 | Input | 1230 | 100 | 0
IoAnaIn_10_override | 0 | Override value | R | 4 | 479 | Holding | 1239 | 100 | 0 | analog_value | 1110 |  | X
IoAnaIn_10_override_en | 0 | Set to 1 to enable override | L | 4 | 482 | Coil | 1226 |  |  | binary_value | 1010 |  | X
IoAnaIn_10_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 487 | Holding | 1243
IoAnaIn_10_hyst | 0 | Hysteresis limit | R | 4 | 490 | Holding | 1244 | 100 | 0
IoAnaIn_11_value |  | Filtered value from sensor | R | 4 | 500 | Input | 1251 | 100 | 0 | analog_value | 1011
IoAnaIn_11_mode | 128 | Mode for input | X | 4 | 503 | Holding | 1251
IoAnaIn_11_unit | 0 | Unit converter | X | 4 | 504 | Holding | 1252
IoAnaIn_11_min_in | -100 | Scale for input | R | 4 | 505 | Holding | 1253 | 100 | 0
IoAnaIn_11_min_out | -100 | Scale for input | R | 4 | 508 | Holding | 1255 | 100 | 0
IoAnaIn_11_max_in | 10000 | Scale for input | R | 4 | 511 | Holding | 1257 | 100 | 0
IoAnaIn_11_max_out | 10000 | Scale for input | R | 4 | 514 | Holding | 1259 | 100 | 0
IoAnaIn_11_prefilter |  | Unfiltered value from sensor | R | 4 | 523 | Input | 1253 | 100 | 0
IoAnaIn_11_raw |  | Raw value from sensor | R | 4 | 526 | Input | 1255 | 100 | 0
IoAnaIn_11_override | 0 | Override value | R | 4 | 529 | Holding | 1264 | 100 | 0 | analog_value | 1111 |  | X
IoAnaIn_11_override_en | 0 | Set to 1 to enable override | L | 4 | 532 | Coil | 1251 |  |  | binary_value | 1011 |  | X
IoAnaIn_11_filter | 5 | Filter time (0 to 17200 seconds) | I | 4 | 537 | Holding | 1268
IoAnaIn_11_hyst | 0 | Hysteresis limit | R | 4 | 540 | Holding | 1269 | 100 | 0
IoAnaIn_11_valueDigits | 2 | Number of shown digits | I | 4 | 546 | Holding | 1271
IoDiIn_1_value |  | Filtered value from sensor | L | 4 | 1000 | Discrete | 1501 |  |  | binary_value | 1101
IoDiIn_1_mode | 130 | Mode for input | X | 4 | 1001 | Holding | 1501
IoDiIn_1_invert | 1 | Invert logic signal | L | 4 | 1002 | Coil | 1501
IoDiIn_1_limit | 900 | Limit for analog value | R | 4 | 1003 | Holding | 1502 | 20 | 0
IoDiIn_1_pulse1 | 0 | Pulse counter 1 | H | 4 | 1006 | Holding | 1503
IoDiIn_1_pulse2 | 0 | Pulse counter 2 | H | 4 | 1009 | Holding | 1505
IoDiIn_1_pulserate | 0 | Pulserate in Hz | R | 4 | 1012 | Holding | 1507 | 100 | 0
IoDiIn_1_override | 0 | Override value | L | 4 | 1016 | Coil | 1503 |  |  | binary_value | 1201 |  | X
IoDiIn_1_override_en | 0 | Set to 1 to enable override | L | 4 | 1017 | Coil | 1504 |  |  | binary_value | 1301 |  | X
IoDiIn_1_hyst | 10 | Hysterisis limit | X | 4 | 1022 | Holding | 1510
IoDiIn_2_value |  | Filtered value from sensor | L | 4 | 1050 | Discrete | 1526 |  |  | binary_value | 1102
IoDiIn_2_mode | 130 | Mode for input | X | 4 | 1051 | Holding | 1526
IoDiIn_2_invert | 1 | Invert logic signal | L | 4 | 1052 | Coil | 1526
IoDiIn_2_limit |  | Limit for analog value | R | 4 | 1053 | Holding | 1527 | 20 | 0
IoDiIn_2_pulse1 | 0 | Pulse counter 1 | H | 4 | 1056 | Holding | 1528
IoDiIn_2_pulse2 | 0 | Pulse counter 2 | H | 4 | 1059 | Holding | 1530
IoDiIn_2_pulserate | 0 | Pulserate in Hz | R | 4 | 1062 | Holding | 1532 | 100 | 0
IoDiIn_2_override | 0 | Override value | L | 4 | 1066 | Coil | 1528 |  |  | binary_value | 1202 |  | X
IoDiIn_2_override_en | 0 | Set to 1 to enable override | L | 4 | 1067 | Coil | 1529 |  |  | binary_value | 1302 |  | X
IoDiIn_2_hyst | 10 | Hysterisis limit | X | 4 | 1072 | Holding | 1535
IoDiIn_3_value |  | Filtered value from sensor | L | 4 | 1100 | Discrete | 1551 |  |  | binary_value | 1103
IoDiIn_3_mode | 130 | Mode for input | X | 4 | 1101 | Holding | 1551
IoDiIn_3_invert | 1 | Invert logic signal | L | 4 | 1102 | Coil | 1551
IoDiIn_3_limit | 180 | Limit for analog value | R | 4 | 1103 | Holding | 1552 | 20 | 0
IoDiIn_3_pulse1 | 0 | Pulse counter 1 | H | 4 | 1106 | Holding | 1553
IoDiIn_3_pulse2 | 0 | Pulse counter 2 | H | 4 | 1109 | Holding | 1555
IoDiIn_3_pulserate | 0 | Pulserate in Hz | R | 4 | 1112 | Holding | 1557 | 100 | 0
IoDiIn_3_override | 0 | Override value | L | 4 | 1116 | Coil | 1553 |  |  | binary_value | 1203 |  | X
IoDiIn_3_override_en | 0 | Set to 1 to enable override | L | 4 | 1117 | Coil | 1554 |  |  | binary_value | 1303 |  | X
IoDiIn_3_hyst | 10 | Hysterisis limit | X | 4 | 1122 | Holding | 1560
IoDiIn_4_value |  | Filtered value from sensor | L | 4 | 1150 | Discrete | 1576 |  |  | binary_value | 1104
IoDiIn_4_mode | 130 | Mode for input | X | 4 | 1151 | Holding | 1576
IoDiIn_4_invert | 0 | Invert logic signal | L | 4 | 1152 | Coil | 1576
IoDiIn_4_pulse1 | 0 | Pulse counter 1 | H | 4 | 1156 | Holding | 1578
IoDiIn_4_pulse2 | 0 | Pulse counter 2 | H | 4 | 1159 | Holding | 1580
IoDiIn_4_pulserate | 0 | Pulserate in Hz | R | 4 | 1162 | Holding | 1582 | 100 | 0
IoDiIn_4_override | 0 | Override value | L | 4 | 1166 | Coil | 1578 |  |  | binary_value | 1204 |  | X
IoDiIn_4_override_en | 0 | Set to 1 to enable override | L | 4 | 1167 | Coil | 1579 |  |  | binary_value | 1304 |  | X
IoAnaOut_1_value | 0 | Value in % set for output | R | 5 | 0 | Holding | 2501 | 100 | 0 | analog_value | 1201 | percent | X
IoAnaOut_1_mode | 1 | Mode for output | X | 5 | 3 | Holding | 2502
IoAnaOut_1_unit | 0 | Unit converter | X | 5 | 4 | Holding | 2503
IoAnaOut_1_min_in | 0 | Scale for output | R | 5 | 5 | Holding | 2504 | 100 | 0
IoAnaOut_1_min_out | 0 | Scale for output | R | 5 | 8 | Holding | 2505 | 100 | 0
IoAnaOut_1_max_in | 100 | Scale for output | R | 5 | 11 | Holding | 2506 | 100 | 0
IoAnaOut_1_max_out | 100 | Scale for output | R | 5 | 14 | Holding | 2507 | 100 | 0
IoAnaOut_1_offset | 0 | Offset for output | R | 5 | 17 | Holding | 2508 | 100 | 0
IoAnaOut_1_default | 0 | Default value if communication is lost | R | 5 | 20 | Holding | 2509 | 100 | 0 | analog_value | 1301 | percent | X
IoAnaOut_1_converted |  | Value converted to SI units from % | R | 5 | 23 | Input | 2501 | 100 | 0 | analog_value | 1401 | volts
IoAnaOut_1_raw |  | Raw value sent to HW | R | 5 | 26 | Input | 2502 | 100 | 0
IoAnaOut_1_override | 0 | Override value | R | 5 | 29 | Holding | 2510 | 100 | 0 | analog_value | 1501 | percent | X
IoAnaOut_1_override_en | 0 | Set to 1 to enable override | L | 5 | 32 | Coil | 2501 |  |  | binary_value | 1401 |  | X
IoAnaOut_1_ramp | 0 | Limits the change in output to this value in units / s. A value of 0 means that the output will not be limited. | R | 5 | 33 | Holding | 2511 | 100 | 0
IoAnaOut_1_pulse_period | 60 | Period time for pulse output | I | 5 | 36 | Holding | 2512
IoAnaOut_2_value | 0 | Value in % set for output | R | 5 | 50 | Holding | 2526 | 100 | 0 | analog_value | 1202 | percent | X
IoAnaOut_2_mode | 1 | Mode for output | X | 5 | 53 | Holding | 2527
IoAnaOut_2_unit | 0 | Unit converter | X | 5 | 54 | Holding | 2528
IoAnaOut_2_min_in | 0 | Scale for output | R | 5 | 55 | Holding | 2529 | 100 | 0
IoAnaOut_2_min_out | 0 | Scale for output | R | 5 | 58 | Holding | 2530 | 100 | 0
IoAnaOut_2_max_in | 100 | Scale for output | R | 5 | 61 | Holding | 2531 | 100 | 0
IoAnaOut_2_max_out | 100 | Scale for output | R | 5 | 64 | Holding | 2532 | 100 | 0
IoAnaOut_2_offset | 0 | Offset for output | R | 5 | 67 | Holding | 2533 | 100 | 0
IoAnaOut_2_default | 0 | Default value if communication is lost | R | 5 | 70 | Holding | 2534 | 100 | 0 | analog_value | 1302 | percent | X
IoAnaOut_2_converted |  | Value converted to SI units from % | R | 5 | 73 | Input | 2526 | 100 | 0 | analog_value | 1402 | volts
IoAnaOut_2_raw |  | Raw value sent to HW | R | 5 | 76 | Input | 2527 | 100 | 0
IoAnaOut_2_override | 0 | Override value | R | 5 | 79 | Holding | 2535 | 100 | 0 | analog_value | 1502 | percent | X
IoAnaOut_2_override_en | 0 | Set to 1 to enable override | L | 5 | 82 | Coil | 2526 |  |  | binary_value | 1402 |  | X
IoAnaOut_2_ramp | 0 | Limits the change in output to this value in units / s. A value of 0 means that the output will not be limited. | R | 5 | 83 | Holding | 2536 | 100 | 0
IoAnaOut_2_pulse_period | 60 | Period time for pulse output | I | 5 | 86 | Holding | 2537
IoAnaOut_3_value | 0 | Value in % set for output | R | 5 | 100 | Holding | 2551 | 100 | 0 | analog_value | 1203 | percent | X
IoAnaOut_3_mode | 1 | Mode for output | X | 5 | 103 | Holding | 2552
IoAnaOut_3_unit | 0 | Unit converter | X | 5 | 104 | Holding | 2553
IoAnaOut_3_min_in | 0 | Scale for output | R | 5 | 105 | Holding | 2554 | 100 | 0
IoAnaOut_3_min_out | 0 | Scale for output | R | 5 | 108 | Holding | 2555 | 100 | 0
IoAnaOut_3_max_in | 100 | Scale for output | R | 5 | 111 | Holding | 2556 | 100 | 0
IoAnaOut_3_max_out | 100 | Scale for output | R | 5 | 114 | Holding | 2557 | 100 | 0
IoAnaOut_3_offset | 0 | Offset for output | R | 5 | 117 | Holding | 2558 | 100 | 0
IoAnaOut_3_default | 0 | Default value if communication is lost | R | 5 | 120 | Holding | 2559 | 100 | 0 | analog_value | 1303 | percent | X
IoAnaOut_3_converted |  | Value converted to SI units from % | R | 5 | 123 | Input | 2551 | 100 | 0 | analog_value | 1403 | volts
IoAnaOut_3_raw |  | Raw value sent to HW | R | 5 | 126 | Input | 2552 | 100 | 0
IoAnaOut_3_override | 0 | Override value | R | 5 | 129 | Holding | 2560 | 100 | 0 | analog_value | 1503 | percent | X
IoAnaOut_3_override_en | 0 | Set to 1 to enable override | L | 5 | 132 | Coil | 2551 |  |  | binary_value | 1403 |  | X
IoAnaOut_3_ramp | 0 | Limits the change in output to this value in units / s. A value of 0 means that the output will not be limited. | R | 5 | 133 | Holding | 2561 | 100 | 0
IoAnaOut_3_pulse_period | 60 | Period time for pulse output | I | 5 | 136 | Holding | 2562
IoAnaOut_4_value | 0 | Value in % set for output | R | 5 | 150 | Holding | 2576 | 100 | 0 | analog_value | 1204 | percent | X
IoAnaOut_4_mode | 1 | Mode for output | X | 5 | 153 | Holding | 2577
IoAnaOut_4_unit | 0 | Unit converter | X | 5 | 154 | Holding | 2578
IoAnaOut_4_min_in | 0 | Scale for output | R | 5 | 155 | Holding | 2579 | 100 | 0
IoAnaOut_4_min_out | 0 | Scale for output | R | 5 | 158 | Holding | 2580 | 100 | 0
IoAnaOut_4_max_in | 100 | Scale for output | R | 5 | 161 | Holding | 2581 | 100 | 0
IoAnaOut_4_max_out | 100 | Scale for output | R | 5 | 164 | Holding | 2582 | 100 | 0
IoAnaOut_4_offset | 0 | Offset for output | R | 5 | 167 | Holding | 2583 | 100 | 0
IoAnaOut_4_default | 0 | Default value if communication is lost | R | 5 | 170 | Holding | 2584 | 100 | 0 | analog_value | 1304 | percent | X
IoAnaOut_4_converted |  | Value converted to SI units from % | R | 5 | 173 | Input | 2576 | 100 | 0 | analog_value | 1404 | volts
IoAnaOut_4_raw |  | Raw value sent to HW | R | 5 | 176 | Input | 2577 | 100 | 0
IoAnaOut_4_override | 0 | Override value | R | 5 | 179 | Holding | 2585 | 100 | 0 | analog_value | 1504 | percent | X
IoAnaOut_4_override_en | 0 | Set to 1 to enable override | L | 5 | 182 | Coil | 2576 |  |  | binary_value | 1404 |  | X
IoAnaOut_4_ramp | 0 | Limits the change in output to this value in units / s. A value of 0 means that the output will not be limited. | R | 5 | 183 | Holding | 2586 | 100 | 0
IoAnaOut_4_pulse_period | 60 | Period time for pulse output | I | 5 | 186 | Holding | 2587
IoDo_1_value | 0 | Value set for output | L | 5 | 1000 | Coil | 3001 |  |  | binary_value | 1501 |  | X
IoDo_1_mode | 3 | Mode for output | X | 5 | 1001 | Holding | 3001
IoDo_1_default | 0 | Default value if communication is lost | L | 5 | 1002 | Coil | 3002 |  |  | binary_value | 1601 |  | X
IoDo_1_override | 0 | Override value | L | 5 | 1003 | Coil | 3003 |  |  | binary_value | 1701 |  | X
IoDo_1_override_en | 0 | Set to 1 to enable override | L | 5 | 1004 | Coil | 3004 |  |  | binary_value | 1801 |  | X
IoDo_1_out |  | Current value of output | L | 5 | 1005 | Discrete | 3001 |  |  | binary_value | 1901
IoDo_1_invert | 0 | Set to 1 to invert output | L | 5 | 1006 | Coil | 3005
IoDo_2_value | 0 | Value set for output | L | 5 | 1050 | Coil | 3026 |  |  | binary_value | 1502 |  | X
IoDo_2_mode | 3 | Mode for output | X | 5 | 1051 | Holding | 3026
IoDo_2_default | 0 | Default value if communication is lost | L | 5 | 1052 | Coil | 3027 |  |  | binary_value | 1602 |  | X
IoDo_2_override | 0 | Override value | L | 5 | 1053 | Coil | 3028 |  |  | binary_value | 1702 |  | X
IoDo_2_override_en | 0 | Set to 1 to enable override | L | 5 | 1054 | Coil | 3029 |  |  | binary_value | 1802 |  | X
IoDo_2_out |  | Current value of output | L | 5 | 1055 | Discrete | 3026 |  |  | binary_value | 1902
IoDo_2_invert | 0 | Set to 1 to invert output | L | 5 | 1056 | Coil | 3030
IoDo_3_value | 0 | Value set for output | L | 5 | 1100 | Coil | 3051 |  |  | binary_value | 1503 |  | X
IoDo_3_mode | 3 | Mode for output | X | 5 | 1101 | Holding | 3051
IoDo_3_default | 0 | Default value if communication is lost | L | 5 | 1102 | Coil | 3052 |  |  | binary_value | 1603 |  | X
IoDo_3_override | 0 | Override value | L | 5 | 1103 | Coil | 3053 |  |  | binary_value | 1703 |  | X
IoDo_3_override_en | 0 | Set to 1 to enable override | L | 5 | 1104 | Coil | 3054 |  |  | binary_value | 1803 |  | X
IoDo_3_out |  | Current value of output | L | 5 | 1105 | Discrete | 3051 |  |  | binary_value | 1903
IoDo_3_invert | 0 | Set to 1 to invert output | L | 5 | 1106 | Coil | 3055
Disp_BrightnessFull | 100 | Display brightness, full (%) | X | 6 | 0 | Holding | 6001 |  |  | analog_value | 8001 | percent | X
Disp_BrightnessDim | 20 | Display brightness, dimmed (%) | X | 6 | 1 | Holding | 6002 |  |  | analog_value | 8011 | percent | X
Disp_TimeFull | 30 | Display time in full mode. 0 = Never dim. | I | 6 | 2 | Holding | 6003 |  |  | analog_value | 8021 | seconds | X
Disp_TimeDim | 30 | Display time in dimmed mode. 0 = Never off. | I | 6 | 4 | Holding | 6004 |  |  | analog_value | 8031 | seconds | X
Disp_BrightnessMax | 60 | Maximum Display brightness, full (%), all other levels will be scaled according to this value | X | 6 | 6
Disp_RgbMax | 60 | Maximum RGB brightness, full (%), all other levels will be scaled according to this value | X | 6 | 7
App_EnableMenuFan | 1 | Enable Fan menu page | X | 10 | 0 | Holding | 7001
App_EnableMenuForcedVent | 1 | Enable Forced ventilation menu page | X | 10 | 1 | Holding | 7002
App_EnableMenuHumidity | 1 | Enable Humidity menu page | X | 10 | 2 | Holding | 7003
App_EnableMenuCO2 | 1 | Enable CO2 menu page | X | 10 | 3 | Holding | 7004
App_EnableMenuVOC | 1 | Enable VOC menu page | X | 10 | 4 | Holding | 7005
App_EnableSetpoint | 1 | Enable setpoint setting from display | X | 10 | 5 | Holding | 7006
App_EnableMenusDebug | 0 | Enable debug menus | X | 10 | 6 | Holding | 7007
QCalib_PLA | 254 |  | X | 217 | 1
QCalib_ELA | 30 |  | X | 217 | 2
QCalib_ModbusAddr | 1 |  | X | 217 | 3
PLA | 254 |  | X | 241 | 0
ELA | 30 |  | X | 241 | 1
Ver_Minor |  |  | X | 241 | 16 | Input | 7
Ver_Major |  |  | X | 241 | 17 | Input | 6
Model |  | Model number | I | 241 | 36 | Input | 2
CPUSpeed | 0 |  | X | 241 | 39
Ver_Branch |  |  | X | 241 | 40 | Input | 8
Ver_Number |  |  | X | 241 | 41 | Input | 9
FeatureLevel | 1 |  | X | 241 | 48
SerialNumberString | 0 |  | $ | 241 | 60
ControllerName | RCX |  | $ | 241 | 63 | Holding | 39
ControllerProject | 0 |  | $ | 241 | 66
ControllerDescription |  | Controller description | $ | 241 | 69
ControllerLocation |  | Controller location | $ | 241 | 72
UptimeMillisec | 0 |  | I | 241 | 75
UptimeSec | 0 |  | H | 241 | 77
GitCommit |  | Internal revision number | I | 241 | 80 | Input | 11
AppCodePage | -535 |  | I | 241 | 98
ModelName | 0 |  | $ | 241 | 100
VendorName | Regin |  | $ | 241 | 109
OSid |  | Application OPERATING_SYSTEM_ID | H | 241 | 138
QsysApplication | RCX |  | $ | 241 | 141
QsysApplicationVersion | 0 |  | $ | 241 | 144
BACnetCommitSettings | 0 | Commit BACnet settings | L | 242 | 59
BACnetDeviceID | -1 | BACnet device ID | H | 242 | 60
BACnetDeviceObjectName | RCX | BACnet device object name | $ | 242 | 63
BACnetSegmentationSupported | 3 | BACnet segmentation supported | X | 242 | 66
BACnetAPDUTimeout | 3000 | BACnet APDU timeout | I | 242 | 67
BACnetAPDUsegmentTimeout | 2000 | BACnet APDU segment timeout | I | 242 | 69
BACnetConfLn | 125 | BACnet configuration load number | X | 242 | 71
BACnetDataLn | 124 | BACnet data load number | X | 242 | 72
BACnetWideCharacterSetEncoding | 0 | BACnet wide character set encoding | X | 242 | 73
BACnetVendorName | AB Regin | BACnet vendor name | $ | 242 | 75
BACnetVendorIdentifier | 264 | BACnet vendor identifier | I | 242 | 78
BACnetMstpMAC_Port_1 | 0 | BACnet MS/TP MAC port 1 | X | 242 | 85
BACnetMstpMaxAPDUlenAccepted_Port_1 | 480 | BACnet MS/TP max accepted APDU length port 1 | I | 242 | 86
BACnetMstpNrOfAPDUretries_Port_1 | 3 | BACnet MS/TP no of APDU retries port 1 | X | 242 | 88
BACnetMstpMaxMasterAddr_Port_1 | 127 | BACnet MS/TP max master address port 1 | X | 242 | 89
BACnetMstpMaxInfoFrames_Port_1 | 1 | BACnet MS/TP max info frames port 1 | X | 242 | 90
BACnetIpEnable | 0 | BACnet IP enable | L | 242 | 112
BACnetMaxServerCOV | 100 | BACnet max server COV | I | 242 | 135
BACnetPassword | gioP5TJBP8FASqREs6zX | BACnet password | $ | 242 | 139
BACnetDatabaseRevisionTicker | 0 | BACnet database revision ticker | I | 242 | 142
ModbusUnitID | 1 | Active Modbus unit ID | X | 242 | 172 | Holding | 2
ModbusCharTimeout_Port_1 | 3 |  | I | 242 | 197 | Holding | 8
ModbusAnswerDelay_Port_1 | 5 |  | I | 242 | 199 | Holding | 9
Mode_Port_1 | 21 | Active RS485 port mode/protocol | X | 248 | 0
Format_Port_1 | 112 | Active RS485 port format | X | 248 | 35
TimeOut_Port_1 | 0 |  | X | 248 | 38
Baud_Port_1 | 0 | Active RS485 port baud rate | X | 248 | 41
Note on C5: 23040 = Do nothing 23041 = Cools reset 23042 = Upgrade 23043 = Colds 23044 = Power up 23045 = Warm reset 23046 = Save config as user default 23047 = Restore config from user default 23048 = Switch to Bluetooth Direct Test Mode
Note on C8: 0 = Inactive 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on C9: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s
Note on C10: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on C16: 0 = Disabled 1 = Set outputs to default values 2 = Set controller state to a default value 3 = Set outputs to default values, start device in offline mode
Note on C20: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on C22: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on C37: 0 = Unit is in auto mode 1 = Unit is in manual mode 2 = Switch to auto mode 3 = Switch to manual mode 4 = Trigger an adc calibration 5 = ADC is performing an calibration
Note on C38: 0 = Always off 1 = Always on 2 = On at startup 3 = On with button press
Note on C64: 0 = Heating mode 1 = Cooling mode
Note on C65: 0 = Heating mode 1 = Cooling mode
Note on C69: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C70: 0 = Controller mode Off 1 = Controller mode Heating 2 = Controller mode Cooling
Note on C71: 0 = Heating mode 1 = Cooling mode
Note on C72: 0 = Heating mode 1 = Cooling mode
Note on C118: 0 = Off 1 = Green 2 = Yellow 3 = Red
Note on C127: 0 = Unused 1 = Room temperature 2 = CO2 Level 3 = Air Flow 4 = Change over medium temperature 5 = Extra Zone Temperature 6 = Supply air temperature 7 = Relative humidity 8 = Damper position 9 = Extract temperature 10 = VAV Change over air temperature 11 = Room temperature 0-10V 12 = VOC index 20 = Presence DI 21 = Window contact DI 22 = Change-over DI 23 = Condensation DI 24 = VAV Change-over DI 25 = Alarm DI
Note on C128: 0 = Unused 1 = Room temperature 2 = CO2 Level 3 = Air Flow 4 = Change over medium temperature 5 = Extra Zone Temperature 6 = Supply air temperature 7 = Relative humidity 8 = Damper position 9 = Extract temperature 10 = VAV Change over air temperature 11 = Room temperature 0-10V 12 = VOC index 20 = Presence DI 21 = Window contact DI 22 = Change-over DI 23 = Condensation DI 24 = VAV Change-over DI 25 = Alarm DI
Note on C129: 0 = Unused 1 = Room temperature 2 = CO2 Level 3 = Air Flow 4 = Change over medium temperature 5 = Extra Zone Temperature 6 = Supply air temperature 7 = Relative humidity 8 = Damper position 9 = Extract temperature 10 = VAV Change over air temperature 11 = Room temperature 0-10V 12 = VOC index 20 = Presence DI 21 = Window contact DI 22 = Change-over DI 23 = Condensation DI 24 = VAV Change-over DI 25 = Alarm DI
Note on C130: 0 = Unused 1 = Room temperature 2 = CO2 Level 3 = Air Flow 4 = Change over medium temperature 5 = Extra Zone Temperature 6 = Supply air temperature 7 = Relative humidity 8 = Damper position 9 = Extract temperature 10 = VAV Change over air temperature 11 = Room temperature 0-10V 12 = VOC index 20 = Presence DI 21 = Window contact DI 22 = Change-over DI 23 = Condensation DI 24 = VAV Change-over DI 25 = Alarm DI
Note on C131: 0 = Unused 1 = Heat 1 output 0-10V 2 = Cool1 output 0-10V 3 = VAV1 output 0-10V 4 = Heat 2 output 0-10V 5 = Cool2 output 0-10V 6 = VAV2 output 0-10V 7 = Change-Over output 0-10V 8 = Heat/Cool 6-way valve output 0-10V 9 = Extra Zone output 0-10V 10 = EC Fan output 0-10V 11 = CO2 control output 0-10V 12 = Humidify output 0-10V 13 = Dehumidify output 0-10V 14 = VAV change-Over output 0-10V 15 = VOC control output 0-10V 20 = Heat 1 output thermal (PWM) 21 = Cool 1 output thermal (PWM) 22 = Heat 2 output thermal (PWM) 23 = Cool 2 output thermal (PWM) 24 = Extra Zone output thermal (PWM) 25 = Change-Over output thermal (PWM) 26 = Heat/Cool 6-way valve output thermal (PWM) 27 = Heat 1 output on/off 28 = Cool 1 output on/off 29 = Heat 2 output on/off 30 = Cool 2 output on/off 31 = Extra Zone output on/off 32 = Fan speed 1 33 = Fan speed 2 34 = Fan speed 3 35 = Forced ventilation 36 = Light control 37 = Extra Zone active 38 = Sum Alarm 50 = CI driver
Note on C132: 0 = Unused 1 = Heat 1 output 0-10V 2 = Cool1 output 0-10V 3 = VAV1 output 0-10V 4 = Heat 2 output 0-10V 5 = Cool2 output 0-10V 6 = VAV2 output 0-10V 7 = Change-Over output 0-10V 8 = Heat/Cool 6-way valve output 0-10V 9 = Extra Zone output 0-10V 10 = EC Fan output 0-10V 11 = CO2 control output 0-10V 12 = Humidify output 0-10V 13 = Dehumidify output 0-10V 14 = VAV change-Over output 0-10V 15 = VOC control output 0-10V 20 = Heat 1 output thermal (PWM) 21 = Cool 1 output thermal (PWM) 22 = Heat 2 output thermal (PWM) 23 = Cool 2 output thermal (PWM) 24 = Extra Zone output thermal (PWM) 25 = Change-Over output thermal (PWM) 26 = Heat/Cool 6-way valve output thermal (PWM) 27 = Heat 1 output on/off 28 = Cool 1 output on/off 29 = Heat 2 output on/off 30 = Cool 2 output on/off 31 = Extra Zone output on/off 32 = Fan speed 1 33 = Fan speed 2 34 = Fan speed 3 35 = Forced ventilation 36 = Light control 37 = Extra Zone active 38 = Sum Alarm 50 = CI driver
Note on C133: 0 = Unused 1 = Heat 1 output 0-10V 2 = Cool1 output 0-10V 3 = VAV1 output 0-10V 4 = Heat 2 output 0-10V 5 = Cool2 output 0-10V 6 = VAV2 output 0-10V 7 = Change-Over output 0-10V 8 = Heat/Cool 6-way valve output 0-10V 9 = Extra Zone output 0-10V 10 = EC Fan output 0-10V 11 = CO2 control output 0-10V 12 = Humidify output 0-10V 13 = Dehumidify output 0-10V 14 = VAV change-Over output 0-10V 15 = VOC control output 0-10V 20 = Heat 1 output thermal (PWM) 21 = Cool 1 output thermal (PWM) 22 = Heat 2 output thermal (PWM) 23 = Cool 2 output thermal (PWM) 24 = Extra Zone output thermal (PWM) 25 = Change-Over output thermal (PWM) 26 = Heat/Cool 6-way valve output thermal (PWM) 27 = Heat 1 output on/off 28 = Cool 1 output on/off 29 = Heat 2 output on/off 30 = Cool 2 output on/off 31 = Extra Zone output on/off 32 = Fan speed 1 33 = Fan speed 2 34 = Fan speed 3 35 = Forced ventilation 36 = Light control 37 = Extra Zone active 38 = Sum Alarm 50 = CI driver
Note on C134: 0 = Unused 1 = Heat 1 output 0-10V 2 = Cool1 output 0-10V 3 = VAV1 output 0-10V 4 = Heat 2 output 0-10V 5 = Cool2 output 0-10V 6 = VAV2 output 0-10V 7 = Change-Over output 0-10V 8 = Heat/Cool 6-way valve output 0-10V 9 = Extra Zone output 0-10V 10 = EC Fan output 0-10V 11 = CO2 control output 0-10V 12 = Humidify output 0-10V 13 = Dehumidify output 0-10V 14 = VAV change-Over output 0-10V 15 = VOC control output 0-10V 20 = Heat 1 output thermal (PWM) 21 = Cool 1 output thermal (PWM) 22 = Heat 2 output thermal (PWM) 23 = Cool 2 output thermal (PWM) 24 = Extra Zone output thermal (PWM) 25 = Change-Over output thermal (PWM) 26 = Heat/Cool 6-way valve output thermal (PWM) 27 = Heat 1 output on/off 28 = Cool 1 output on/off 29 = Heat 2 output on/off 30 = Cool 2 output on/off 31 = Extra Zone output on/off 32 = Fan speed 1 33 = Fan speed 2 34 = Fan speed 3 35 = Forced ventilation 36 = Light control 37 = Extra Zone active 38 = Sum Alarm 50 = CI driver
Note on C135: 0 = Unused 1 = Heat 1 2 = Cool1 3 = VAV1 4 = Heat 2 5 = Cool2 6 = VAV2 7 = Change-Over 8 = Heat/Cool 6-way valve 9 = Change-Over VAV
Note on C136: 0 = Unused 1 = Heat 1 2 = Cool1 3 = VAV1 4 = Heat 2 5 = Cool2 6 = VAV2 7 = Change-Over 8 = Heat/Cool 6-way valve 9 = Change-Over VAV
Note on C137: 0 = Unused 1 = Heat 1 2 = Cool1 3 = VAV1 4 = Heat 2 5 = Cool2 6 = VAV2 7 = Change-Over 8 = Heat/Cool 6-way valve 9 = Change-Over VAV
Note on C176: 0 = Manual heating 1 = Manual cooling 2 = Digital input 3 = Analog input, simple 4 = Analog input, advanced
Note on C181: 0 = Manual heating 1 = Manual cooling 2 = Digital input 3 = Analog input, simple 4 = Analog input, advanced
Note on C205: 0 = Unused 1 = Heat 2 = Cool
Note on C211: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C222: 0 = Unused 1 = Active when heating 2 = Active when cooling 3 = Active when heating and cooling
Note on C229: 0 = No Control 1 = Controlled by heating 2 = Controlled by Cooling 3 = Controlled by both heating and cooling
Note on C230: 0 = Fan off 1 = Fan at low speed 2 = Fan at medium speed 3 = Fan at high speed 4 = Fan in Auto mode
Note on C243: 0 = No Control 1 = Controlled by heating 2 = Controlled by Cooling 3 = Controlled by both heating and cooling
Note on C254: 0 = Unused 1 = Active when cooling or heating is over limit 2 = Active when cooling is over limit
Note on C256: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C257: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C258: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C259: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C260: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C284: 0 = Heating mode 1 = Cooling mode
Note on C285: 0 = Heating mode 1 = Cooling mode
Note on C302: 0 = Off 1 = Manual 2 = Auto
Note on C303: 0 = Off 1 = Manual 2 = Auto
Note on C304: 0 = Off 1 = Manual 2 = Auto
Note on C305: 0 = Off 1 = Manual 2 = Auto
Note on C306: 0 = Off 1 = Manual 2 = Auto
Note on C307: 0 = Off 1 = Manual 2 = Auto
Note on C308: 0 = Off 1 = Manual 2 = Auto
Note on C309: 0 = Off 1 = Manual 2 = Auto
Note on C310: 0 = Off 1 = Manual 2 = Auto
Note on C311: 0 = Off 1 = Manual 2 = Auto
Note on C312: 0 = Off 1 = Manual 2 = Auto
Note on C313: 0 = Off 1 = Manual 2 = Auto
Note on C314: 0 = Off 1 = Manual 2 = Auto
Note on C315: 0 = Off 1 = Manual 2 = Auto
Note on C316: 0 = Off 1 = Manual 2 = Auto
Note on C322: 0 = Never 1 = Regularly 2 = Regularly and power up 3 = Regularly and power up and state change to Occupied
Note on C348: 0 = Actual temperature 1 = Heat setpoint 2 = Cool setpoint 3 = Average value of heating and cooling setpoint 4 = Setpoint offset 5 = CO2 level 6 = Heat setpoint + offset 7 = Cool setpoint + offset 8 = Average setpoint + offset 9 = Calculated air flow 10 = Active setpoint + offset
Note on C349: 0 = Setpoint offset 1 = Active setpoint + offset 2 = Heat setpoint + offset 3 = Cool setpoint + offset 4 = Heat occupied setpoint + offset 5 = Cool occupied setpoint + offset 6 = Average setpoint + offset
Note on C350: 0 = Off 1 = Manual 2 = Auto
Note on C351: 0 = Off 1 = Manual 2 = Auto
Note on C352: 0 = Off 1 = Manual 2 = Auto
Note on C353: 0 = Off 1 = Manual 2 = Auto
Note on C354: 0 = Off 1 = Manual 2 = Auto
Note on C355: 0 = Off 1 = Manual 2 = Auto
Note on C356: 0 = Off 1 = Manual 2 = Auto
Note on C357: 0 = Off 1 = Manual 2 = Auto
Note on C358: 0 = Off 1 = Manual 2 = Auto
Note on C359: 0 = Off 1 = Manual 2 = Auto
Note on C360: 0 = Off 1 = Manual 2 = Auto
Note on C361: 0 = Off 1 = Manual 2 = Auto
Note on C362: 0 = Off 1 = Manual 2 = Auto
Note on C363: 0 = Off 1 = Manual 2 = Auto
Note on C364: 0 = Off 1 = Manual 2 = Auto
Note on C365: 0 = Off 1 = Manual 2 = Auto
Note on C366: 0 = Off 1 = Manual 2 = Auto
Note on C367: 0 = Off 1 = Manual 2 = Auto
Note on C385: 0 = Always off 1 = Show only when the value is displayed 2 = Always on
Note on C395: 0 = Off 1 = Manual 2 = Auto
Note on C396: 0 = Off 1 = Manual 2 = Auto
Note on C397: 0 = Off 1 = Unoccupied 2 = Standby 3 = Occupied 4 = Bypass 5 = Unused
Note on C407: 0 = Off 1 = Dehumidify 2 = Humidify
Note on C410: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C411: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C425: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C426: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C440: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C441: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C454: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C455: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C468: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C469: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C481: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C482: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C494: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C495: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C507: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C508: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C521: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C522: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C534: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C535: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C547: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C548: 0 = Keep default unit 1 = Convert PT1000 to Fahrenheit 2 = Convert PT1000 to Celsius 3 = Convert NI1000 (DIN) to Fahrenheit 4 = Convert NI1000 (DIN) to Celsius 5 = Convert pressure to millimeter H2O (water column) 6 = Convert pressure to millibar 7 = Convert pressure to inch H2O (water column) 8 = Convert NI1000 (LG) to Fahrenheit 9 = Convert NI1000 (LG) to Celsius
Note on C561: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C571: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C581: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C591: 0 = Disabled 3 = Pt1000/Ni1000, measurement unit range in resistance 9 = Voltage, measurement unit range in volt 128 = I2C sensor 129 = SPI sensor 130 = Digital input 131 = Input from DPAC value 132 = Current measurement on UI 133 = Condensation input 134 = 0-10kOhm input 135 = Internal value
Note on C599: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C600: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V
Note on C614: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C615: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V
Note on C629: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C630: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V
Note on C644: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C645: 0 = 0% = 0V, 100% = 10V 1 = 0% = 0V, 100% = 5V 2 = 0% = 2V, 100% = 10V 3 = 0% = 0mA, 100% = 20mA 4 = 0% = 4mA, 100% = 20mA 5 = <50% = 0V, >50% = 10V 6 = <50% = 0V, >50% = 5V 7 = 0% = 10V, 100% = 0V 8 = 0% = 05V, 100% = 0V 9 = 0% = 10V, 100% = 2V
Note on C659: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C666: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C673: 0 = Disabled, use as digital? 1 = Normal 0-10V output 2 = 0 -20 mA output 3 = Two discrete voltage levels 4 = Output to DPAC 5 = Use channel to drive CI sensor 6 = Pulse output (PWM)
Note on C685: 0 = Disabled 1 = Enabled 2 = Read only
Note on C686: 0 = Disabled 1 = Enabled 2 = Read only
Note on C687: 0 = Disabled 1 = Enabled 2 = Read only
Note on C688: 0 = Disabled 1 = Enabled 2 = Read only
Note on C689: 0 = Disabled 1 = Enabled 2 = Read only
Note on C690: 0 = Disabled 1 = Enabled 2 = Read only
Note on C691: 0 = Disabled 1 = Enabled 2 = Read only
Note on C741: 0 = Inactive 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on C742: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on C744: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s
Note on K5: 23041 = Do nothing 23042 = Cools reset 23043 = Upgrade 23044 = Colds 23045 = Power up 23046 = Warm reset 23047 = Save config as user default 23048 = Restore config from user default 23049 = Switch to Bluetooth Direct Test Mode
Note on K8: 1 = Inactive 14 = BACnet 16 = Modbus slave 22 = EXOline/Modbus autodetect
Note on K9: 1 = 9600 bits/s 3 = 2400 bits/s 4 = 1200 bits/s 16 = 19200 bits/s 18 = 38400 bits/s 19 = 57600 bits/s 21 = 115200 bits/s 22 = 230400 bits/s 23 = 460800 bits/s 26 = 921k6 bits/s 27 = 1000000 bits/s 28 = 250000 bits/s
Note on K10: 17 = 8 bit, no parity, 1 stop bit 25 = 8 bit, no parity, 2 stop bits 49 = 8 bit, even parity, 1 stop bit 57 = 8 bit, even parity, 2 stop bits 113 = 8 bit, odd parity, 1 stop bit 121 = 8 bit, odd parity, 2 stop bits
Note on K16: 1 = Disabled 2 = Set outputs to default values 3 = Set controller state to a default value 4 = Set outputs to default values, start device in offline mode
Note on K64: 1 = Heating mode 2 = Cooling mode
Note on K65: 1 = Heating mode 2 = Cooling mode
Note on K69: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on K70: 1 = Controller mode Off 2 = Controller mode Heating 3 = Controller mode Cooling
Note on K71: 1 = Heating mode 2 = Cooling mode
Note on K72: 1 = Heating mode 2 = Cooling mode
Note on K118: 1 = Off 2 = Green 3 = Yellow 4 = Red
Note on K230: 1 = Fan off 2 = Fan at low speed 3 = Fan at medium speed 4 = Fan at high speed 5 = Fan in Auto mode
Note on K256: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on K257: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on K258: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on K259: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on K260: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused
Note on K284: 1 = Heating mode 2 = Cooling mode
Note on K285: 1 = Heating mode 2 = Cooling mode
Note on K302: 1 = Off 2 = Manual 3 = Auto
Note on K303: 1 = Off 2 = Manual 3 = Auto
Note on K304: 1 = Off 2 = Manual 3 = Auto
Note on K305: 1 = Off 2 = Manual 3 = Auto
Note on K306: 1 = Off 2 = Manual 3 = Auto
Note on K307: 1 = Off 2 = Manual 3 = Auto
Note on K309: 1 = Off 2 = Manual 3 = Auto
Note on K310: 1 = Off 2 = Manual 3 = Auto
Note on K311: 1 = Off 2 = Manual 3 = Auto
Note on K312: 1 = Off 2 = Manual 3 = Auto
Note on K313: 1 = Off 2 = Manual 3 = Auto
Note on K314: 1 = Off 2 = Manual 3 = Auto
Note on K315: 1 = Off 2 = Manual 3 = Auto
Note on K348: 1 = Actual temperature 2 = Heat setpoint 3 = Cool setpoint 4 = Average value of heating and cooling setpoint 5 = Setpoint offset 6 = CO2 level 7 = Heat setpoint + offset 8 = Cool setpoint + offset 9 = Average setpoint + offset 10 = Calculated air flow 11 = Active setpoint + offset
Note on K349: 1 = Setpoint offset 2 = Active setpoint + offset 3 = Heat setpoint + offset 4 = Cool setpoint + offset 5 = Heat occupied setpoint + offset 6 = Cool occupied setpoint + offset 7 = Average setpoint + offset
Note on K350: 1 = Off 2 = Manual 3 = Auto
Note on K351: 1 = Off 2 = Manual 3 = Auto
Note on K352: 1 = Off 2 = Manual 3 = Auto
Note on K353: 1 = Off 2 = Manual 3 = Auto
Note on K354: 1 = Off 2 = Manual 3 = Auto
Note on K355: 1 = Off 2 = Manual 3 = Auto
Note on K356: 1 = Off 2 = Manual 3 = Auto
Note on K357: 1 = Off 2 = Manual 3 = Auto
Note on K358: 1 = Off 2 = Manual 3 = Auto
Note on K359: 1 = Off 2 = Manual 3 = Auto
Note on K360: 1 = Off 2 = Manual 3 = Auto
Note on K361: 1 = Off 2 = Manual 3 = Auto
Note on K362: 1 = Off 2 = Manual 3 = Auto
Note on K364: 1 = Off 2 = Manual 3 = Auto
Note on K366: 1 = Off 2 = Manual 3 = Auto
Note on K367: 1 = Off 2 = Manual 3 = Auto
Note on K395: 1 = Off 2 = Manual 3 = Auto
Note on K396: 1 = Off 2 = Manual 3 = Auto
Note on K397: 1 = Off 2 = Unoccupied 3 = Standby 4 = Occupied 5 = Bypass 6 = Unused