## Variables
RUX-… 2.1-1-xx - Variable list | [17 empty] | Revision: | A
|  |  |  | EXOline |  |  | Modbus | [6 empty] | BACnet
Name | Default | Storage | Description | Type | Load | Cell | Reg. Type | RW | Register | Addr | Data Type | Scale | Offset | Default BACnet name | Object type | Instance | Unit | Writeable | Variable type
ZERO_DUMMY |  | RO | Modbus list version | X | 1 | 0 | Holding | R | 300001 | 0 | U8
ModbusListVersion |  | RO | Modbus list version | X | 1 | 0 | Input | R | 300001 | 0 | U8
product_reset | 0 |  | Write to this register will trigger resets with different reset reasons | I | 1 | 1
rc_wink | 0 |  | Wink for this amount of time in seconds | X | 1 | 3 | Holding | RW | 400003 | 2 | U8 |  |  | Wink | positive_integer_value | 9011 |  | X
RC_CommSettingsCommit | 0 |  | Commit communication settings | L | 1 | 5 | Coil | RW | 000001 | 0 | LOGIC |  |  | CommCommit | binary_value | 9001 |  | X
RC_Port1Mode | 2 |  | Comm. protocol Port 1 (RS485) | X | 1 | 6 | Holding | RW | 400005 | 4 | U8 |  |  | Port1Mode | multi_state_value | 9001 |  | X
RC_Port1Baud | 0 |  | Comm. speed Port 1 (RS485) | X | 1 | 7 | Holding | RW | 400007 | 6 | U8 |  |  | Port1Baud | multi_state_value | 9101 |  | X
RC_Port1Format | 112 |  | Comm. format Port 1 (RS485) | X | 1 | 8 | Holding | RW | 400006 | 5 | U8 |  |  | Port1Format | multi_state_value | 9201 |  | X
SerialHigh |  | RO | Serial number, high part | I | 1 | 15 | Input | R | 300005 | 4 | I16
SerialMid |  | RO | Serial number, mid part | I | 1 | 17 | Input | R | 300004 | 3 | I16
SerialLow |  | RO | Serial number, low part | I | 1 | 19 | Input | R | 300003 | 2 | I16
RC_Offline |  | RO | Heartbeat function indicates if the device is offline or not | L | 1 | 21 | Discrete | R | 100001 | 0 | LOGIC
RC_OfflineTrigger | 0 |  | Write 1 to this register periodically for keep system running in normal mode, will be set to 0 by application | L | 1 | 22 | Coil | RW | 000002 | 1 | LOGIC |  |  | HeartbeatTrigger | binary_value | 9101 |  | X
RC_OfflineFunction | 0 | CONF | Offline function | X | 1 | 23 | Holding | RW | 400020 | 19 | U8 |  |  | RC_OfflineFunction | multi_state_value | 9301 |  | X
RC_OfflineCounter |  |  | Offline timeout counter seconds. Used to check current state of the counter, it counts from 0 at trigger up to next trigger or HEARTBEAT_OFFLINE_TIMEOUT. | I | 1 | 24 | Input | R | 300010 | 9 | I16
RC_OfflineTimeout | 10 | CONF | Offline timeout in seconds. External application must write to HEARTBEAT_OFFLINE_TRIGGER within this time to keep regulator in normal mode. | I | 1 | 26 | Holding | RW | 400021 | 20 | I16
RgbEnable | 0 |  | Set to True to enable the external control of the LED | L | 1 | 35 | Coil | RW | 000003 | 2 | LOGIC
RgbOffColor | 0 | CONF | 8 bit color for when the LED is in state Off (0bRRRGGGBB) | X | 1 | 36 | Holding | RW | 400027 | 26 | U8
RgbOffTime | 500 | CONF | Off time in ms | I | 1 | 37 | Holding | RW | 400028 | 27 | I16
RgbOnColor | 252 | CONF | 8 bit color for when the LED is in state On (0bRRRGGGBB) | X | 1 | 39 | Holding | RW | 400029 | 28 | U8
RgbOnTime | 100 | CONF | On time in ms | I | 1 | 40 | Holding | RW | 400030 | 29 | I16
product_status | 0 | RO | Bit field, See Description on Global device Status | I | 1 | 58 | Holding | RW | 400004 | 3 | I16
RafosVerMajor |  | RO | Platform software version, major part | X | 1 | 64 | Input | R | 300013 | 12 | U8
RafosVerMinor |  | RO | Platform software version, minor part | X | 1 | 65 | Input | R | 300014 | 13 | U8
RafosVerBranch |  | RO | Platform software version, branch part | X | 1 | 66 | Input | R | 300015 | 14 | U8
RafosVerNumber |  | RO | Platform software version, number part | X | 1 | 67 | Input | R | 300016 | 15 | U8
RafosGitCommit |  | RO | Platform Git commit | I | 1 | 68 | Input | R | 300017 | 16 | I16
OsId |  | RO | Application OPERATING_SYSTEM_ID | I | 1 | 70 | Input | R | 300021 | 20 | I16
VersionNumberString |  | RO | The application version as a string | $ | 1 | 76
gitCommitHashString |  | RO | The Full Git hash of the application | $ | 1 | 79
BleButtonMode | 3 | CONF | Function for BLE button | X | 1 | 83 | Holding | RW | 400071 | 70 | U8
BleButtonTimeout | 120 | CONF | Timeout when BLE is started with the button | I | 1 | 84 | Holding | RW | 400072 | 71 | I16
BleVerMajor |  | RO | BLE stack version, major part | X | 1 | 98 | Input | R | 300022 | 21 | U8
BleVerMinor |  | RO | BLE stack version, minor part | X | 1 | 99 | Input | R | 300023 | 22 | U8
BleVerBranch |  | RO | BLE stack version, branch part | X | 1 | 100 | Input | R | 300024 | 23 | U8
BleVerNumber |  | RO | BLE stack version, number part | X | 1 | 101 | Input | R | 300025 | 24 | U8
FusVerMajor |  | RO | FUS stack version, major part | X | 1 | 102 | Input | R | 300026 | 25 | U8
FusVerMinor |  | RO | FUS version, minor part | X | 1 | 103 | Input | R | 300027 | 26 | U8
FusVerBranch |  | RO | FUS version, branch part | X | 1 | 104 | Input | R | 300028 | 27 | U8
FusVerNumber |  | RO | FUS version, number part | X | 1 | 105 | Input | R | 300029 | 28 | U8
ble_power | 35 | CONF | BLE TX power level | X | 1 | 108 | Holding | RW | 400082 | 81 | U8
disable_nv_storage | 0 | CONF | Set to 1 to disable storage in non volatile memory | L | 1 | 109 | Coil | RW | 000005 | 4 | LOGIC
RC_RoomTemp |  | RO | Room temperature | R | 2 | 0 | Input | R | 305001 | 5000 | I16SO | 10 | 0 | RC_RoomTemp | analog_value | 10002 | degrees_celsius
RC_CO2Level |  | RO | Room CO2 level | R | 2 | 3 | Input | R | 305002 | 5001 | I16SO | 1 | 0 | RC_CO2Level | analog_value | 10011 | parts_per_million
RC_Humidity |  | RO | Relative humidity | R | 2 | 21 | Input | R | 305008 | 5007 | I16SO | 10 | 0 | RC_Humidity | analog_value | 10071 | percent_relative_humidity
RC_RoomActiveSetpoint |  | RO | Active room control setpoint | R | 2 | 31 | Input | R | 305009 | 5008 | I16SO | 10 | 0 | RC_RoomActiveSetpoint | analog_value | 10081 | degrees_celsius
RC_FanSpeed |  | RO | Current 3-speed fan speed | X | 2 | 73 | Input | R | 305030 | 5029 | U8
RC_VOC |  | RO | VOC index | R | 2 | 87 | Input | R | 305033 | 5032 | I16SO | 10 | 0 | RC_VOC | analog_value | 10281
RC_DisplayViewValue |  | RO | Value to be shown in the display | R | 2 | 90 | Input | R | 305034 | 5033 | I16SO | 10 | 0 | RC_DisplayViewValue | analog_value | 10291
RC_DisplaySetpointValue |  | RO | Setpoint display at setpoint adjustment | R | 2 | 93 | Input | R | 305035 | 5034 | I16SO | 10 | 0 | RC_DisplaySetpointValue | analog_value | 10301
RC_CO2Indicator |  | RO | RGB CO2 indication | X | 2 | 96 | Input | R | 305036 | 5035 | U8 |  |  | RC_CO2Indicator | multi_state_value | 10021
RC_RoomSetpointHeatOff | 8 | CONF | Heating setpoint in Off state (frost protection). | R | 3 | 184 | Holding | RW | 405149 | 5148 | I16SO | 10 | 0 | RC_RoomSetpointHeatOff | analog_value | 10331 | degrees_celsius | X
RC_RoomSetpointHeatUnoccupied | 15 | CONF | Heating setpoint in Unoccupied state. | R | 3 | 187 | Holding | RW | 405150 | 5149 | I16SO | 10 | 0 | RC_RoomSetpointHeatUnoccupied | analog_value | 10341 | degrees_celsius | X
RC_RoomSetpointHeatStandby | 19 | CONF | Heating setpoint in Standby state. | R | 3 | 190 | Holding | RW | 405151 | 5150 | I16SO | 10 | 0 | RC_RoomSetpointHeatStandby | analog_value | 10351 | degrees_celsius | X
RC_RoomSetpointHeatOccupied | 22 | CONF | Heating setpoint in Occupied state. | R | 3 | 193 | Holding | RW | 405152 | 5151 | I16SO | 10 | 0 | RC_RoomSetpointHeatOccupied | analog_value | 10361 | degrees_celsius | X
RC_RoomSetpointCoolUnoccupied | 30 | CONF | Cooling setpoint in Unoccupied state. | R | 3 | 196 | Holding | RW | 405153 | 5152 | I16SO | 10 | 0 | RC_RoomSetpointCoolUnoccupied | analog_value | 10371 | degrees_celsius | X
RC_RoomSetpointCoolStandby | 27 | CONF | Cooling setpoint in Standby state. | R | 3 | 199 | Holding | RW | 405154 | 5153 | I16SO | 10 | 0 | RC_RoomSetpointCoolStandby | analog_value | 10381 | degrees_celsius | X
RC_RoomSetpointCoolOccupied | 24 | CONF | Cooling setpoint in Occupied state. | R | 3 | 202 | Holding | RW | 405155 | 5154 | I16SO | 10 | 0 | RC_RoomSetpointCoolOccupied | analog_value | 10391 | degrees_celsius | X
RC_RoomSetpointOffset | 0 | CONF | Setpoint offset. Effective in Standby state or higher. | R | 3 | 205 | Holding | RW | 405156 | 5155 | I16SO | 10 | 0 | RC_RoomSetpointOffset | analog_value | 10401 | degrees_celsius | X
RC_RoomSetpointOffsetMaxPos | 3 | CONF | Maximum positive setpoint offset. | R | 3 | 208 | Holding | RW | 405157 | 5156 | I16SO | 10 | 0 | RC_RoomSetpointOffsetMaxPos | analog_value | 10411 | degrees_celsius | X
RC_RoomSetpointOffsetMaxNeg | 3 | CONF | Maximum negative setpoint offset. | R | 3 | 211 | Holding | RW | 405158 | 5157 | I16SO | 10 | 0 | RC_RoomSetpointOffsetMaxNeg | analog_value | 10421 | degrees_celsius | X
RC_FanSelect | 4 | CONF | Fan speed setting | X | 3 | 281 | Holding | RW | 405185 | 5184 | U8 |  |  | RC_FanSelect | multi_state_value | 10031
RC_RoomTempRemote | 22 |  | Remote setting of room temperature | R | 3 | 318 | Holding | RW | 405210 | 5209 | I16SO | 10 | 0 | RC_RoomTempRemote | analog_value | 10611 | degrees_celsius | X
RC_CO2LevelRemote | 400 |  | Remote setting of room CO2 level | R | 3 | 321 | Holding | RW | 405211 | 5210 | I16SO | 10 | 0 | RC_CO2LevelRemote | analog_value | 10621 | parts_per_million | X
RC_HumidityRemote | 50 |  | Remote setting of relative humidity | R | 3 | 339 | Holding | RW | 405217 | 5216 | I16SO | 10 | 0 | RC_HumidityRemote | analog_value | 10681 | percent_relative_humidity | X
RC_VOCRemote | 100 |  | Remote setting of VOC index | R | 3 | 342 | Holding | RW | 405218 | 5217 | I16SO | 10 | 0 | RC_VOCRemote | analog_value | 10691 |  | X
RC_RoomTempRemoteSelect | 0 | CONF | Enable remote setting of room temperature | L | 3 | 345 | Coil | RW | 005022 | 5021 | LOGIC |  |  | RC_RoomTempRemoteSelect | binary_value | 10321 |  | X
RC_CO2LevelRemoteSelect | 0 | CONF | Enable remote setting of room CO2 level | L | 3 | 346 | Coil | RW | 005023 | 5022 | LOGIC |  |  | RC_CO2LevelRemoteSelect | binary_value | 10331 |  | X
RC_HumidityRemoteSelect | 0 | CONF | Enable remote setting of relative humidity | L | 3 | 352 | Coil | RW | 005029 | 5028 | LOGIC |  |  | RC_HumidityRemoteSelect | binary_value | 10391 |  | X
RC_VOCRemoteSelect | 0 | CONF | Enable remote setting of VOC index | L | 3 | 353 | Coil | RW | 005030 | 5029 | LOGIC |  |  | RC_VOCRemoteSelect | binary_value | 10401 |  | X
RC_DisplayViewMode | 0 | CONF | Select value to be shown in the display | X | 3 | 442 | Holding | RW | 405271 | 5270 | U8 |  |  | RC_DisplayViewMode | multi_state_value | 10221 |  | X
RC_DisplaySetpointMode | 0 | CONF | Select setpoint display at setpoint adjustment | X | 3 | 443 | Holding | RW | 405272 | 5271 | U8 |  |  | RC_DisplaySetpointMode | multi_state_value | 10231 |  | X
RC_CO2FilterTime | 5 | CONF | CO2 filter time (0 to 17200 seconds) | I | 3 | 492 | Holding | RW | 405301 | 5300 | I16
RC_RHFilterTime | 5 | CONF | RH filter time (0 to 17200 seconds) | I | 3 | 494 | Holding | RW | 405302 | 5301 | I16
RC_TempFilterTime | 5 | CONF | Temperature filter time (0 to 17200 seconds) | I | 3 | 496 | Holding | RW | 405303 | 5302 | I16
RC_VOCFilterTime | 5 | CONF | VOC index filter time (0 to 17200 seconds) | I | 3 | 500 | Holding | RW | 405305 | 5304 | I16
RC_CO2LevelYellow | 800 | CONF | CO2 level for yellow led | R | 3 | 502 | Holding | RW | 405306 | 5305 | I16SO | 1 | 0 | RC_CO2LevelYellow | analog_value | 10891 | parts_per_million | X
RC_CO2LevelRed | 1000 | CONF | CO2 level for red led | R | 3 | 505 | Holding | RW | 405307 | 5306 | I16SO | 1 | 0 | RC_CO2LevelRed | analog_value | 10901 | parts_per_million | X
RC_CO2SetIndication | 0 | CONF | Enable/disable CO2 led indication | X | 3 | 508 | Holding | RW | 405308 | 5307 | U8
RC_RuxControllerMode | 0 | CONF | Current controller mode for RUX devices | X | 3 | 550 | Holding | RW | 405325 | 5324 | U8
IoAnaIn_5_value |  | RO | Room temperature from internal sensor | R | 4 | 200 | Input | R | 301101 301102 | 1100 1101 | REGx2I32SO | 100 | 0 | IoAnaIn_5_value | analog_value | 1005
IoAnaIn_6_value |  | RO | Room humidity from internal sensor | R | 4 | 250 | Input | R | 301126 301127 | 1125 1126 | REGx2I32SO | 100 | 0 | IoAnaIn_6_value | analog_value | 1006
IoAnaIn_7_value |  | RO | Room VOC from internal sensor | R | 4 | 300 | Input | R | 301151 301152 | 1150 1151 | REGx2I32SO | 100 | 0 | IoAnaIn_7_value | analog_value | 1007
IoAnaIn_8_value |  | RO | Room CO2 from internal sensor | R | 4 | 350 | Input | R | 301176 301177 | 1175 1176 | REGx2I32SO | 100 | 0 | IoAnaIn_8_value | analog_value | 1008
Disp_BrightnessFull | 100 | CONF | Display brightness, full (%) | X | 6 | 0 | Holding | RW | 406001 | 6000 | U8 |  |  | Disp_BrightnessFull | analog_value | 8001 | percent | X
Disp_BrightnessDim | 20 | CONF | Display brightness, dimmed (%) | X | 6 | 1 | Holding | RW | 406002 | 6001 | U8 |  |  | Disp_BrightnessDim | analog_value | 8011 | percent | X
Disp_TimeFull | 30 | CONF | Display time in full mode. 0 = Never dim. | I | 6 | 2 | Holding | RW | 406003 | 6002 | I16 |  |  | Disp_TimeFull | analog_value | 8021 | seconds | X
Disp_TimeDim | 30 | CONF | Display time in dimmed mode. 0 = Never off. | I | 6 | 4 | Holding | RW | 406004 | 6003 | I16 |  |  | Disp_TimeDim | analog_value | 8031 | seconds | X
DisplayStartupMode | 4 | CONF | What to display during device startup | X | 6 | 8 | Holding | RW | 406005 | 6004 | U8
rt_text_font | 0 | CONF | What font to use for the display text | X | 8 | 275 | Holding | RW | 408145 | 8144 | U8 |  |  | rt_text_font | multi_state_value | 11000 |  | X
rt_text_mode | 0 | CONF | Single or dual row text in display | X | 8 | 276 | Holding | RW | 408146 | 8145 | U8 |  |  | rt_text_mode | multi_state_value | 11001 |  | X
rt_text_display_scroll_mode | 0 | CONF | Scroll mode | X | 8 | 277 | Holding | RW | 408147 | 8146 | U8 |  |  | rt_text_display_scroll_mode | multi_state_value | 11002 |  | X
rt_text_display_scroll_speed | 100 | CONF | Time in ms between scrolling one pixel | I | 8 | 278 | Holding | RW | 408148 | 8147 | I16 |  |  | rt_text_display_scroll_speed | analog_value | 11007 | milliseconds | X
rt_text_visability | 0 | CONF | When to show the custom text | X | 8 | 280 | Holding | RW | 408149 | 8148 | U8 |  |  | rt_text_visability | multi_state_value | 11003 |  | X
rt_text_timeleft | 0 |  | Time to show the custom text | I | 8 | 281 | Holding | RW | 408150 | 8149 | I16 |  |  | rt_text_timeleft | analog_value | 11008 | seconds | X
rt_text_row_1 |  | CONF | String to show on row 1 in the display | $ | 8 | 283 | Holding | RW | 408151 - 408182 | 8150 - 8181 | STRING |  |  | rt_text_row_1 | characterstring_value | 11000 |  | X
rt_text_row_2 |  | CONF | String to show on row 2 in the display | $ | 8 | 286 | Holding | RW | 408183 - 408214 | 8182 - 8213 | STRING |  |  | rt_text_row_2 | characterstring_value | 11001 |  | X
rt_fb_visability | 0 | CONF | When to show the custom frame buffer | X | 8 | 289 | Holding | RW | 408215 | 8214 | U8 |  |  | rt_fb_visability | multi_state_value | 11004 |  | X
rt_fb_timeleft | 0 |  | Time to show the custom frame buffer | I | 8 | 290 | Holding | RW | 408216 | 8215 | I16 |  |  | rt_fb_timeleft | analog_value | 11009 | seconds | X
rt_fb_row0 | 0 |  | Frame buffer data for row 0 on the display | H | 8 | 292 | Holding | RW | 408217 408218 | 8216 8217 | REGx2I32 |  |  | rt_fb_row0 | analog_value | 11010 | seconds | X
rt_fb_row1 | 0 |  | Frame buffer data for row 1 on the display | H | 8 | 295 | Holding | RW | 408219 408220 | 8218 8219 | REGx2I32 |  |  | rt_fb_row1 | analog_value | 11011 | seconds | X
rt_fb_row2 | 0 |  | Frame buffer data for row 2 on the display | H | 8 | 298 | Holding | RW | 408221 408222 | 8220 8221 | REGx2I32 |  |  | rt_fb_row2 | analog_value | 11012 | seconds | X
rt_fb_row3 | 0 |  | Frame buffer data for row 3 on the display | H | 8 | 301 | Holding | RW | 408223 408224 | 8222 8223 | REGx2I32 |  |  | rt_fb_row3 | analog_value | 11013 | seconds | X
rt_fb_row4 | 0 |  | Frame buffer data for row 4 on the display | H | 8 | 304 | Holding | RW | 408225 408226 | 8224 8225 | REGx2I32 |  |  | rt_fb_row4 | analog_value | 11014 | seconds | X
rt_fb_row5 | 0 |  | Frame buffer data for row 5 on the display | H | 8 | 307 | Holding | RW | 408227 408228 | 8226 8227 | REGx2I32 |  |  | rt_fb_row5 | analog_value | 11015 | seconds | X
rt_fb_row6 | 0 |  | Frame buffer data for row 6 on the display | H | 8 | 310 | Holding | RW | 408229 408230 | 8228 8229 | REGx2I32 |  |  | rt_fb_row6 | analog_value | 11016 | seconds | X
rt_fb_row7 | 0 |  | Frame buffer data for row 7 on the display | H | 8 | 313 | Holding | RW | 408231 408232 | 8230 8231 | REGx2I32 |  |  | rt_fb_row7 | analog_value | 11017 | seconds | X
rt_fb_row8 | 0 |  | Frame buffer data for row 8 on the display | H | 8 | 316 | Holding | RW | 408233 408234 | 8232 8233 | REGx2I32 |  |  | rt_fb_row8 | analog_value | 11018 | seconds | X
rt_fb_row9 | 0 |  | Frame buffer data for row 9 on the display | H | 8 | 319 | Holding | RW | 408235 408236 | 8234 8235 | REGx2I32 |  |  | rt_fb_row9 | analog_value | 11019 | seconds | X
rt_fb_row10 | 0 |  | Frame buffer data for row 10 on the display | H | 8 | 322 | Holding | RW | 408237 408238 | 8236 8237 | REGx2I32 |  |  | rt_fb_row10 | analog_value | 11020 | seconds | X
App_EnableMenuFan | 1 | CONF | Enable Fan menu page | X | 10 | 0 | Holding | RW | 407001 | 7000 | U8
App_EnableMenuForcedVent | 1 | CONF | Enable Forced ventilation menu page | X | 10 | 1 | Holding | RW | 407002 | 7001 | U8
App_EnableMenuHumidity | 1 | CONF | Enable Humidity menu page | X | 10 | 2 | Holding | RW | 407003 | 7002 | U8
App_EnableMenuCO2 | 1 | CONF | Enable CO2 menu page | X | 10 | 3 | Holding | RW | 407004 | 7003 | U8
App_EnableMenuVOC | 1 | CONF | Enable VOC menu page | X | 10 | 4 | Holding | RW | 407005 | 7004 | U8
App_EnableSetpoint | 1 | CONF | Enable setpoint setting from display | X | 10 | 5 | Holding | RW | 407006 | 7005 | U8
App_EnableMenuMode | 0 | CONF | Enable Mode menu page | X | 10 | 7 | Holding | RW | 407008 | 7007 | U8
App_ModeMenuTitle | MODE | CONF | Mode menu title | $ | 10 | 8
App_ModeMenuAutoText | AUTO | CONF | Mode menu Auto state text | $ | 10 | 11
App_ModeMenuOffText | OFF | CONF | Mode menu Off state text | $ | 10 | 14
App_ModeMenuUnoccText | OFF | CONF | Mode menu Unoccupied state text | $ | 10 | 17
App_ModeMenuStandbyText | ECO | CONF | Mode menu Standby state text | $ | 10 | 20
App_ModeMenuOccText | ON | CONF | Mode menu Occupied state text | $ | 10 | 23
App_ModeMenuBypassText | MAX | CONF | Mode menu Bypass state text | $ | 10 | 26
App_ModeMenuOffEnable | 1 | CONF | Mode menu Off state enable | L | 10 | 29
App_ModeMenuUnoccEnable | 0 | CONF | Mode menu Unoccupied state enable | L | 10 | 30
App_ModeMenuStandbyEnable | 0 | CONF | Mode menu Standby state enable | L | 10 | 31
App_ModeMenuOccEnable | 1 | CONF | Mode menu Occupied state enable | L | 10 | 32
App_ModeMenuBypassEnable | 0 | CONF | Mode menu Bypass state enable | L | 10 | 33
SCD40_ASC_enable | 1 | CONF | Enable automatic calibration of CO2 sensor | L | 10 | 50 | Coil | RW | 000101 | 100 | LOGIC
SCD40_ASC_target | 400 | CONF | Automatic calibration of CO2 sensor target | I | 10 | 51 | Holding | RW | 400101 | 100 | I16
SCD40_factory_reset | 1 |  | Set to one to run factory reset of CO2 sensor, will reset to 0 after reset | L | 10 | 53 | Coil | RW | 000102 | 101 | LOGIC
SCD40_FRC_result | 0 |  | Calculated offset after calibration or -9999 if failed. | I | 10 | 54 | Holding | RW | 400102 | 101 | I16
SCD40_FRC_enable | 0 |  | Set to 1 to start forced recalibration of CO2 sensor, will be reset to 0 when done | L | 10 | 56 | Coil | RW | 000103 | 102 | LOGIC
SCD40_FRC_target | 400 |  | Current actual CO2 value to calibrate to | I | 10 | 57 | Holding | RW | 400103 | 102 | I16
App_EnableMenuTemp | 0 | CONF | Enable Temperature menu page | X | 10 | 64 | Holding | RW | 407010 | 7009 | U8
CM1Title |  | CONF | Title for Custom Menu 1 | $ | 10 | 200
CM1Alt1Text |  | CONF | Text for alternative 1 for Custom Menu 1 | $ | 10 | 203
CM1Alt1Value | 0 | CONF | Value for alternative 1 for Custom Menu 1 | I | 10 | 206 | Holding | RW | 407011 | 7010 | I16
CM1Alt2Text |  | CONF | Text for alternative 2 for Custom Menu 1 | $ | 10 | 208
CM1Alt2Value | 0 | CONF | Value for alternative 2 for Custom Menu 1 | I | 10 | 211 | Holding | RW | 407012 | 7011 | I16
CM1Alt3Text |  | CONF | Text for alternative 3 for Custom Menu 1 | $ | 10 | 213
CM1Alt3Value | 0 | CONF | Value for alternative 3 for Custom Menu 1 | I | 10 | 216 | Holding | RW | 407013 | 7012 | I16
CM1Alt4Text |  | CONF | Text for alternative 4 for Custom Menu 1 | $ | 10 | 218
CM1Alt4Value | 0 | CONF | Value for alternative 4 for Custom Menu 1 | I | 10 | 221 | Holding | RW | 407014 | 7013 | I16
CM1Alt5Text |  | CONF | Text for alternative 5 for Custom Menu 1 | $ | 10 | 223
CM1Alt5Value | 0 | CONF | Value for alternative 5 for Custom Menu 1 | I | 10 | 226 | Holding | RW | 407015 | 7014 | I16
CM1Alt6Text |  | CONF | Text for alternative 6 for Custom Menu 1 | $ | 10 | 228
CM1Alt6Value | 0 | CONF | Value for alternative 6 for Custom Menu 1 | I | 10 | 231 | Holding | RW | 407016 | 7015 | I16
CM1Alt7Text |  | CONF | Text for alternative 7 for Custom Menu 1 | $ | 10 | 233
CM1Alt7Value | 0 | CONF | Value for alternative 7 for Custom Menu 1 | I | 10 | 236 | Holding | RW | 407017 | 7016 | I16
CM1Alt8Text |  | CONF | Text for alternative 8 for Custom Menu 1 | $ | 10 | 238
CM1Alt8Value | 0 | CONF | Value for alternative 8 for Custom Menu 1 | I | 10 | 241 | Holding | RW | 407018 | 7017 | I16
CM1Alt9Text |  | CONF | Text for alternative 9 for Custom Menu 1 | $ | 10 | 243
CM1Alt9Value | 0 | CONF | Value for alternative 9 for Custom Menu 1 | I | 10 | 246 | Holding | RW | 407019 | 7018 | I16
CM1Alt10Text |  | CONF | Text for alternative 10 for Custom Menu 1 | $ | 10 | 248
CM1Alt10Value | 0 | CONF | Value for alternative 10 for Custom Menu 1 | I | 10 | 251 | Holding | RW | 407020 | 7019 | I16
CM1Alt11Text |  | CONF | Text for alternative 11 for Custom Menu 1 | $ | 10 | 253
CM1Alt11Value | 0 | CONF | Value for alternative 11 for Custom Menu 1 | I | 10 | 256 | Holding | RW | 407021 | 7020 | I16
CM1Alt12Text |  | CONF | Text for alternative 12 for Custom Menu 1 | $ | 10 | 258
CM1Alt12Value | 0 | CONF | Value for alternative 12 for Custom Menu 1 | I | 10 | 261 | Holding | RW | 407022 | 7021 | I16
CM1Alt13Text |  | CONF | Text for alternative 13 for Custom Menu 1 | $ | 10 | 263
CM1Alt13Value | 0 | CONF | Value for alternative 13 for Custom Menu 1 | I | 10 | 266 | Holding | RW | 407023 | 7022 | I16
CM1Alt14Text |  | CONF | Text for alternative 14 for Custom Menu 1 | $ | 10 | 268
CM1Alt14Value | 0 | CONF | Value for alternative 14 for Custom Menu 1 | I | 10 | 271 | Holding | RW | 407024 | 7023 | I16
CM1Alt15Text |  | CONF | Text for alternative 15 for Custom Menu 1 | $ | 10 | 273
CM1Alt15Value | 0 | CONF | Value for alternative 15 for Custom Menu 1 | I | 10 | 276 | Holding | RW | 407025 | 7024 | I16
CM1Alt16Text |  | CONF | Text for alternative 16 for Custom Menu 1 | $ | 10 | 278
CM1Alt16Value | 0 | CONF | Value for alternative 16 for Custom Menu 1 | I | 10 | 281 | Holding | RW | 407026 | 7025 | I16
CM1Alt17Text |  | CONF | Text for alternative 17 for Custom Menu 1 | $ | 10 | 283
CM1Alt17Value | 0 | CONF | Value for alternative 17 for Custom Menu 1 | I | 10 | 286 | Holding | RW | 407027 | 7026 | I16
CM1Alt18Text |  | CONF | Text for alternative 18 for Custom Menu 1 | $ | 10 | 288
CM1Alt18Value | 0 | CONF | Value for alternative 18 for Custom Menu 1 | I | 10 | 291 | Holding | RW | 407028 | 7027 | I16
CM1Alt19Text |  | CONF | Text for alternative 19 for Custom Menu 1 | $ | 10 | 293
CM1Alt19Value | 0 | CONF | Value for alternative 19 for Custom Menu 1 | I | 10 | 296 | Holding | RW | 407029 | 7028 | I16
CM1Alt20Text |  | CONF | Text for alternative 20 for Custom Menu 1 | $ | 10 | 298
CM1Alt20Value | 0 | CONF | Value for alternative 20 for Custom Menu 1 | I | 10 | 301 | Holding | RW | 407030 | 7029 | I16
CM1Alt21Text |  | CONF | Text for alternative 21 for Custom Menu 1 | $ | 10 | 303
CM1Alt21Value | 0 | CONF | Value for alternative 21 for Custom Menu 1 | I | 10 | 306 | Holding | RW | 407031 | 7030 | I16
CM1CurrentAlt | 0 | CONF | Current alternative for Custom Menu 1 | I | 10 | 308 | Holding | RW | 407032 | 7031 | I16 |  |  | CM1CurrentAlt | analog_value | 8040 |  | X
CM1CurrentValue | 0 | CONF | Current value for Custom Menu 1 | I | 10 | 310 | Holding | RW | 407033 | 7032 | I16 |  |  | CM1CurrentValue | analog_value | 8041 |  | X
CM1Enabled | 0 | CONF | Enable Custom Menu 1 | L | 10 | 312 | Coil | RW | 007006 | 7005 | U8
CM2Title |  | CONF | Title for Custom Menu 2 | $ | 10 | 400
CM2Alt1Text |  | CONF | Text for alternative 1 for Custom Menu 2 | $ | 10 | 403
CM2Alt1Value | 0 | CONF | Value for alternative 1 for Custom Menu 2 | I | 10 | 406 | Holding | RW | 407034 | 7033 | I16
CM2Alt2Text |  | CONF | Text for alternative 2 for Custom Menu 2 | $ | 10 | 408
CM2Alt2Value | 0 | CONF | Value for alternative 2 for Custom Menu 2 | I | 10 | 411 | Holding | RW | 407035 | 7034 | I16
CM2Alt3Text |  | CONF | Text for alternative 3 for Custom Menu 2 | $ | 10 | 413
CM2Alt3Value | 0 | CONF | Value for alternative 3 for Custom Menu 2 | I | 10 | 416 | Holding | RW | 407036 | 7035 | I16
CM2Alt4Text |  | CONF | Text for alternative 4 for Custom Menu 2 | $ | 10 | 418
CM2Alt4Value | 0 | CONF | Value for alternative 4 for Custom Menu 2 | I | 10 | 421 | Holding | RW | 407037 | 7036 | I16
CM2Alt5Text |  | CONF | Text for alternative 5 for Custom Menu 2 | $ | 10 | 423
CM2Alt5Value | 0 | CONF | Value for alternative 5 for Custom Menu 2 | I | 10 | 426 | Holding | RW | 407038 | 7037 | I16
CM2Alt6Text |  | CONF | Text for alternative 6 for Custom Menu 2 | $ | 10 | 428
CM2Alt6Value | 0 | CONF | Value for alternative 6 for Custom Menu 2 | I | 10 | 431 | Holding | RW | 407039 | 7038 | I16
CM2Alt7Text |  | CONF | Text for alternative 7 for Custom Menu 2 | $ | 10 | 433
CM2Alt7Value | 0 | CONF | Value for alternative 7 for Custom Menu 2 | I | 10 | 436 | Holding | RW | 407040 | 7039 | I16
CM2Alt8Text |  | CONF | Text for alternative 8 for Custom Menu 2 | $ | 10 | 438
CM2Alt8Value | 0 | CONF | Value for alternative 8 for Custom Menu 2 | I | 10 | 441 | Holding | RW | 407041 | 7040 | I16
CM2Alt9Text |  | CONF | Text for alternative 9 for Custom Menu 2 | $ | 10 | 443
CM2Alt9Value | 0 | CONF | Value for alternative 9 for Custom Menu 2 | I | 10 | 446 | Holding | RW | 407042 | 7041 | I16
CM2Alt10Text |  | CONF | Text for alternative 10 for Custom Menu 2 | $ | 10 | 448
CM2Alt10Value | 0 | CONF | Value for alternative 10 for Custom Menu 2 | I | 10 | 451 | Holding | RW | 407043 | 7042 | I16
CM2Alt11Text |  | CONF | Text for alternative 11 for Custom Menu 2 | $ | 10 | 453
CM2Alt11Value | 0 | CONF | Value for alternative 11 for Custom Menu 2 | I | 10 | 456 | Holding | RW | 407044 | 7043 | I16
CM2Alt12Text |  | CONF | Text for alternative 12 for Custom Menu 2 | $ | 10 | 458
CM2Alt12Value | 0 | CONF | Value for alternative 12 for Custom Menu 2 | I | 10 | 461 | Holding | RW | 407045 | 7044 | I16
CM2Alt13Text |  | CONF | Text for alternative 13 for Custom Menu 2 | $ | 10 | 463
CM2Alt13Value | 0 | CONF | Value for alternative 13 for Custom Menu 2 | I | 10 | 466 | Holding | RW | 407046 | 7045 | I16
CM2Alt14Text |  | CONF | Text for alternative 14 for Custom Menu 2 | $ | 10 | 468
CM2Alt14Value | 0 | CONF | Value for alternative 14 for Custom Menu 2 | I | 10 | 471 | Holding | RW | 407047 | 7046 | I16
CM2Alt15Text |  | CONF | Text for alternative 15 for Custom Menu 2 | $ | 10 | 473
CM2Alt15Value | 0 | CONF | Value for alternative 15 for Custom Menu 2 | I | 10 | 476 | Holding | RW | 407048 | 7047 | I16
CM2Alt16Text |  | CONF | Text for alternative 16 for Custom Menu 2 | $ | 10 | 478
CM2Alt16Value | 0 | CONF | Value for alternative 16 for Custom Menu 2 | I | 10 | 481 | Holding | RW | 407049 | 7048 | I16
CM2Alt17Text |  | CONF | Text for alternative 17 for Custom Menu 2 | $ | 10 | 483
CM2Alt17Value | 0 | CONF | Value for alternative 17 for Custom Menu 2 | I | 10 | 486 | Holding | RW | 407050 | 7049 | I16
CM2Alt18Text |  | CONF | Text for alternative 18 for Custom Menu 2 | $ | 10 | 488
CM2Alt18Value | 0 | CONF | Value for alternative 18 for Custom Menu 2 | I | 10 | 491 | Holding | RW | 407051 | 7050 | I16
CM2Alt19Text |  | CONF | Text for alternative 19 for Custom Menu 2 | $ | 10 | 493
CM2Alt19Value | 0 | CONF | Value for alternative 19 for Custom Menu 2 | I | 10 | 496 | Holding | RW | 407052 | 7051 | I16
CM2Alt20Text |  | CONF | Text for alternative 20 for Custom Menu 2 | $ | 10 | 498
CM2Alt20Value | 0 | CONF | Value for alternative 20 for Custom Menu 2 | I | 10 | 501 | Holding | RW | 407053 | 7052 | I16
CM2Alt21Text |  | CONF | Text for alternative 21 for Custom Menu 2 | $ | 10 | 503
CM2Alt21Value | 0 | CONF | Value for alternative 21 for Custom Menu 2 | I | 10 | 506 | Holding | RW | 407054 | 7053 | I16
CM2CurrentAlt | 0 | CONF | Current alternative for Custom Menu 2 | I | 10 | 508 | Holding | RW | 407055 | 7054 | I16 |  |  | CM2CurrentAlt | analog_value | 8042 |  | X
CM2CurrentValue | 0 | CONF | Current value for Custom Menu 2 | I | 10 | 510 | Holding | RW | 407056 | 7055 | I16 |  |  | CM2CurrentValue | analog_value | 8043 |  | X
CM2Enabled | 0 | CONF | Enable Custom Menu 2 | L | 10 | 512 | Coil | RW | 007007 | 7006 | U8
CM3Title |  | CONF | Title for Custom Menu 3 | $ | 10 | 600
CM3Alt1Text |  | CONF | Text for alternative 1 for Custom Menu 3 | $ | 10 | 603
CM3Alt1Value | 0 | CONF | Value for alternative 1 for Custom Menu 3 | I | 10 | 606 | Holding | RW | 407057 | 7056 | I16
CM3Alt2Text |  | CONF | Text for alternative 2 for Custom Menu 3 | $ | 10 | 608
CM3Alt2Value | 0 | CONF | Value for alternative 2 for Custom Menu 3 | I | 10 | 611 | Holding | RW | 407058 | 7057 | I16
CM3Alt3Text |  | CONF | Text for alternative 3 for Custom Menu 3 | $ | 10 | 613
CM3Alt3Value | 0 | CONF | Value for alternative 3 for Custom Menu 3 | I | 10 | 616 | Holding | RW | 407059 | 7058 | I16
CM3Alt4Text |  | CONF | Text for alternative 4 for Custom Menu 3 | $ | 10 | 618
CM3Alt4Value | 0 | CONF | Value for alternative 4 for Custom Menu 3 | I | 10 | 621 | Holding | RW | 407060 | 7059 | I16
CM3Alt5Text |  | CONF | Text for alternative 5 for Custom Menu 3 | $ | 10 | 623
CM3Alt5Value | 0 | CONF | Value for alternative 5 for Custom Menu 3 | I | 10 | 626 | Holding | RW | 407061 | 7060 | I16
CM3Alt6Text |  | CONF | Text for alternative 6 for Custom Menu 3 | $ | 10 | 628
CM3Alt6Value | 0 | CONF | Value for alternative 6 for Custom Menu 3 | I | 10 | 631 | Holding | RW | 407062 | 7061 | I16
CM3Alt7Text |  | CONF | Text for alternative 7 for Custom Menu 3 | $ | 10 | 633
CM3Alt7Value | 0 | CONF | Value for alternative 7 for Custom Menu 3 | I | 10 | 636 | Holding | RW | 407063 | 7062 | I16
CM3Alt8Text |  | CONF | Text for alternative 8 for Custom Menu 3 | $ | 10 | 638
CM3Alt8Value | 0 | CONF | Value for alternative 8 for Custom Menu 3 | I | 10 | 641 | Holding | RW | 407064 | 7063 | I16
CM3Alt9Text |  | CONF | Text for alternative 9 for Custom Menu 3 | $ | 10 | 643
CM3Alt9Value | 0 | CONF | Value for alternative 9 for Custom Menu 3 | I | 10 | 646 | Holding | RW | 407065 | 7064 | I16
CM3Alt10Text |  | CONF | Text for alternative 10 for Custom Menu 3 | $ | 10 | 648
CM3Alt10Value | 0 | CONF | Value for alternative 10 for Custom Menu 3 | I | 10 | 651 | Holding | RW | 407066 | 7065 | I16
CM3Alt11Text |  | CONF | Text for alternative 11 for Custom Menu 3 | $ | 10 | 653
CM3Alt11Value | 0 | CONF | Value for alternative 11 for Custom Menu 3 | I | 10 | 656 | Holding | RW | 407067 | 7066 | I16
CM3Alt12Text |  | CONF | Text for alternative 12 for Custom Menu 3 | $ | 10 | 658
CM3Alt12Value | 0 | CONF | Value for alternative 12 for Custom Menu 3 | I | 10 | 661 | Holding | RW | 407068 | 7067 | I16
CM3Alt13Text |  | CONF | Text for alternative 13 for Custom Menu 3 | $ | 10 | 663
CM3Alt13Value | 0 | CONF | Value for alternative 13 for Custom Menu 3 | I | 10 | 666 | Holding | RW | 407069 | 7068 | I16
CM3Alt14Text |  | CONF | Text for alternative 14 for Custom Menu 3 | $ | 10 | 668
CM3Alt14Value | 0 | CONF | Value for alternative 14 for Custom Menu 3 | I | 10 | 671 | Holding | RW | 407070 | 7069 | I16
CM3Alt15Text |  | CONF | Text for alternative 15 for Custom Menu 3 | $ | 10 | 673
CM3Alt15Value | 0 | CONF | Value for alternative 15 for Custom Menu 3 | I | 10 | 676 | Holding | RW | 407071 | 7070 | I16
CM3Alt16Text |  | CONF | Text for alternative 16 for Custom Menu 3 | $ | 10 | 678
CM3Alt16Value | 0 | CONF | Value for alternative 16 for Custom Menu 3 | I | 10 | 681 | Holding | RW | 407072 | 7071 | I16
CM3Alt17Text |  | CONF | Text for alternative 17 for Custom Menu 3 | $ | 10 | 683
CM3Alt17Value | 0 | CONF | Value for alternative 17 for Custom Menu 3 | I | 10 | 686 | Holding | RW | 407073 | 7072 | I16
CM3Alt18Text |  | CONF | Text for alternative 18 for Custom Menu 3 | $ | 10 | 688
CM3Alt18Value | 0 | CONF | Value for alternative 18 for Custom Menu 3 | I | 10 | 691 | Holding | RW | 407074 | 7073 | I16
CM3Alt19Text |  | CONF | Text for alternative 19 for Custom Menu 3 | $ | 10 | 693
CM3Alt19Value | 0 | CONF | Value for alternative 19 for Custom Menu 3 | I | 10 | 696 | Holding | RW | 407075 | 7074 | I16
CM3Alt20Text |  | CONF | Text for alternative 20 for Custom Menu 3 | $ | 10 | 698
CM3Alt20Value | 0 | CONF | Value for alternative 20 for Custom Menu 3 | I | 10 | 701 | Holding | RW | 407076 | 7075 | I16
CM3Alt21Text |  | CONF | Text for alternative 21 for Custom Menu 3 | $ | 10 | 703
CM3Alt21Value | 0 | CONF | Value for alternative 21 for Custom Menu 3 | I | 10 | 706 | Holding | RW | 407077 | 7076 | I16
CM3CurrentAlt | 0 | CONF | Current alternative for Custom Menu 3 | I | 10 | 708 | Holding | RW | 407078 | 7077 | I16 |  |  | CM3CurrentAlt | analog_value | 8044 |  | X
CM3CurrentValue | 0 | CONF | Current value for Custom Menu 3 | I | 10 | 710 | Holding | RW | 407079 | 7078 | I16 |  |  | CM3CurrentValue | analog_value | 8045 |  | X
CM3Enabled | 0 | CONF | Enable Custom Menu 3 | L | 10 | 712 | Coil | RW | 007008 | 7007 | U8
CM4Title |  | CONF | Title for Custom Menu 4 | $ | 10 | 800
CM4Alt1Text |  | CONF | Text for alternative 1 for Custom Menu 4 | $ | 10 | 803
CM4Alt1Value | 0 | CONF | Value for alternative 1 for Custom Menu 4 | I | 10 | 806 | Holding | RW | 407080 | 7079 | I16
CM4Alt2Text |  | CONF | Text for alternative 2 for Custom Menu 4 | $ | 10 | 808
CM4Alt2Value | 0 | CONF | Value for alternative 2 for Custom Menu 4 | I | 10 | 811 | Holding | RW | 407081 | 7080 | I16
CM4Alt3Text |  | CONF | Text for alternative 3 for Custom Menu 4 | $ | 10 | 813
CM4Alt3Value | 0 | CONF | Value for alternative 3 for Custom Menu 4 | I | 10 | 816 | Holding | RW | 407082 | 7081 | I16
CM4Alt4Text |  | CONF | Text for alternative 4 for Custom Menu 4 | $ | 10 | 818
CM4Alt4Value | 0 | CONF | Value for alternative 4 for Custom Menu 4 | I | 10 | 821 | Holding | RW | 407083 | 7082 | I16
CM4Alt5Text |  | CONF | Text for alternative 5 for Custom Menu 4 | $ | 10 | 823
CM4Alt5Value | 0 | CONF | Value for alternative 5 for Custom Menu 4 | I | 10 | 826 | Holding | RW | 407084 | 7083 | I16
CM4Alt6Text |  | CONF | Text for alternative 6 for Custom Menu 4 | $ | 10 | 828
CM4Alt6Value | 0 | CONF | Value for alternative 6 for Custom Menu 4 | I | 10 | 831 | Holding | RW | 407085 | 7084 | I16
CM4Alt7Text |  | CONF | Text for alternative 7 for Custom Menu 4 | $ | 10 | 833
CM4Alt7Value | 0 | CONF | Value for alternative 7 for Custom Menu 4 | I | 10 | 836 | Holding | RW | 407086 | 7085 | I16
CM4Alt8Text |  | CONF | Text for alternative 8 for Custom Menu 4 | $ | 10 | 838
CM4Alt8Value | 0 | CONF | Value for alternative 8 for Custom Menu 4 | I | 10 | 841 | Holding | RW | 407087 | 7086 | I16
CM4Alt9Text |  | CONF | Text for alternative 9 for Custom Menu 4 | $ | 10 | 843
CM4Alt9Value | 0 | CONF | Value for alternative 9 for Custom Menu 4 | I | 10 | 846 | Holding | RW | 407088 | 7087 | I16
CM4Alt10Text |  | CONF | Text for alternative 10 for Custom Menu 4 | $ | 10 | 848
CM4Alt10Value | 0 | CONF | Value for alternative 10 for Custom Menu 4 | I | 10 | 851 | Holding | RW | 407089 | 7088 | I16
CM4Alt11Text |  | CONF | Text for alternative 11 for Custom Menu 4 | $ | 10 | 853
CM4Alt11Value | 0 | CONF | Value for alternative 11 for Custom Menu 4 | I | 10 | 856 | Holding | RW | 407090 | 7089 | I16
CM4Alt12Text |  | CONF | Text for alternative 12 for Custom Menu 4 | $ | 10 | 858
CM4Alt12Value | 0 | CONF | Value for alternative 12 for Custom Menu 4 | I | 10 | 861 | Holding | RW | 407091 | 7090 | I16
CM4Alt13Text |  | CONF | Text for alternative 13 for Custom Menu 4 | $ | 10 | 863
CM4Alt13Value | 0 | CONF | Value for alternative 13 for Custom Menu 4 | I | 10 | 866 | Holding | RW | 407092 | 7091 | I16
CM4Alt14Text |  | CONF | Text for alternative 14 for Custom Menu 4 | $ | 10 | 868
CM4Alt14Value | 0 | CONF | Value for alternative 14 for Custom Menu 4 | I | 10 | 871 | Holding | RW | 407093 | 7092 | I16
CM4Alt15Text |  | CONF | Text for alternative 15 for Custom Menu 4 | $ | 10 | 873
CM4Alt15Value | 0 | CONF | Value for alternative 15 for Custom Menu 4 | I | 10 | 876 | Holding | RW | 407094 | 7093 | I16
CM4Alt16Text |  | CONF | Text for alternative 16 for Custom Menu 4 | $ | 10 | 878
CM4Alt16Value | 0 | CONF | Value for alternative 16 for Custom Menu 4 | I | 10 | 881 | Holding | RW | 407095 | 7094 | I16
CM4Alt17Text |  | CONF | Text for alternative 17 for Custom Menu 4 | $ | 10 | 883
CM4Alt17Value | 0 | CONF | Value for alternative 17 for Custom Menu 4 | I | 10 | 886 | Holding | RW | 407096 | 7095 | I16
CM4Alt18Text |  | CONF | Text for alternative 18 for Custom Menu 4 | $ | 10 | 888
CM4Alt18Value | 0 | CONF | Value for alternative 18 for Custom Menu 4 | I | 10 | 891 | Holding | RW | 407097 | 7096 | I16
CM4Alt19Text |  | CONF | Text for alternative 19 for Custom Menu 4 | $ | 10 | 893
CM4Alt19Value | 0 | CONF | Value for alternative 19 for Custom Menu 4 | I | 10 | 896 | Holding | RW | 407098 | 7097 | I16
CM4Alt20Text |  | CONF | Text for alternative 20 for Custom Menu 4 | $ | 10 | 898
CM4Alt20Value | 0 | CONF | Value for alternative 20 for Custom Menu 4 | I | 10 | 901 | Holding | RW | 407099 | 7098 | I16
CM4Alt21Text |  | CONF | Text for alternative 21 for Custom Menu 4 | $ | 10 | 903
CM4Alt21Value | 0 | CONF | Value for alternative 21 for Custom Menu 4 | I | 10 | 906 | Holding | RW | 407100 | 7099 | I16
CM4CurrentAlt | 0 | CONF | Current alternative for Custom Menu 4 | I | 10 | 908 | Holding | RW | 407101 | 7100 | I16 |  |  | CM4CurrentAlt | analog_value | 8046 |  | X
CM4CurrentValue | 0 | CONF | Current value for Custom Menu 4 | I | 10 | 910 | Holding | RW | 407102 | 7101 | I16 |  |  | CM4CurrentValue | analog_value | 8047 |  | X
CM4Enabled | 0 | CONF | Enable Custom Menu 4 | L | 10 | 912 | Coil | RW | 007009 | 7008 | U8
CM5Title |  | CONF | Title for Custom Menu 5 | $ | 10 | 1000
CM5Alt1Text |  | CONF | Text for alternative 1 for Custom Menu 5 | $ | 10 | 1003
CM5Alt1Value | 0 | CONF | Value for alternative 1 for Custom Menu 5 | I | 10 | 1006 | Holding | RW | 407103 | 7102 | I16
CM5Alt2Text |  | CONF | Text for alternative 2 for Custom Menu 5 | $ | 10 | 1008
CM5Alt2Value | 0 | CONF | Value for alternative 2 for Custom Menu 5 | I | 10 | 1011 | Holding | RW | 407104 | 7103 | I16
CM5Alt3Text |  | CONF | Text for alternative 3 for Custom Menu 5 | $ | 10 | 1013
CM5Alt3Value | 0 | CONF | Value for alternative 3 for Custom Menu 5 | I | 10 | 1016 | Holding | RW | 407105 | 7104 | I16
CM5Alt4Text |  | CONF | Text for alternative 4 for Custom Menu 5 | $ | 10 | 1018
CM5Alt4Value | 0 | CONF | Value for alternative 4 for Custom Menu 5 | I | 10 | 1021 | Holding | RW | 407106 | 7105 | I16
CM5Alt5Text |  | CONF | Text for alternative 5 for Custom Menu 5 | $ | 10 | 1023
CM5Alt5Value | 0 | CONF | Value for alternative 5 for Custom Menu 5 | I | 10 | 1026 | Holding | RW | 407107 | 7106 | I16
CM5Alt6Text |  | CONF | Text for alternative 6 for Custom Menu 5 | $ | 10 | 1028
CM5Alt6Value | 0 | CONF | Value for alternative 6 for Custom Menu 5 | I | 10 | 1031 | Holding | RW | 407108 | 7107 | I16
CM5Alt7Text |  | CONF | Text for alternative 7 for Custom Menu 5 | $ | 10 | 1033
CM5Alt7Value | 0 | CONF | Value for alternative 7 for Custom Menu 5 | I | 10 | 1036 | Holding | RW | 407109 | 7108 | I16
CM5Alt8Text |  | CONF | Text for alternative 8 for Custom Menu 5 | $ | 10 | 1038
CM5Alt8Value | 0 | CONF | Value for alternative 8 for Custom Menu 5 | I | 10 | 1041 | Holding | RW | 407110 | 7109 | I16
CM5Alt9Text |  | CONF | Text for alternative 9 for Custom Menu 5 | $ | 10 | 1043
CM5Alt9Value | 0 | CONF | Value for alternative 9 for Custom Menu 5 | I | 10 | 1046 | Holding | RW | 407111 | 7110 | I16
CM5Alt10Text |  | CONF | Text for alternative 10 for Custom Menu 5 | $ | 10 | 1048
CM5Alt10Value | 0 | CONF | Value for alternative 10 for Custom Menu 5 | I | 10 | 1051 | Holding | RW | 407112 | 7111 | I16
CM5Alt11Text |  | CONF | Text for alternative 11 for Custom Menu 5 | $ | 10 | 1053
CM5Alt11Value | 0 | CONF | Value for alternative 11 for Custom Menu 5 | I | 10 | 1056 | Holding | RW | 407113 | 7112 | I16
CM5Alt12Text |  | CONF | Text for alternative 12 for Custom Menu 5 | $ | 10 | 1058
CM5Alt12Value | 0 | CONF | Value for alternative 12 for Custom Menu 5 | I | 10 | 1061 | Holding | RW | 407114 | 7113 | I16
CM5Alt13Text |  | CONF | Text for alternative 13 for Custom Menu 5 | $ | 10 | 1063
CM5Alt13Value | 0 | CONF | Value for alternative 13 for Custom Menu 5 | I | 10 | 1066 | Holding | RW | 407115 | 7114 | I16
CM5Alt14Text |  | CONF | Text for alternative 14 for Custom Menu 5 | $ | 10 | 1068
CM5Alt14Value | 0 | CONF | Value for alternative 14 for Custom Menu 5 | I | 10 | 1071 | Holding | RW | 407116 | 7115 | I16
CM5Alt15Text |  | CONF | Text for alternative 15 for Custom Menu 5 | $ | 10 | 1073
CM5Alt15Value | 0 | CONF | Value for alternative 15 for Custom Menu 5 | I | 10 | 1076 | Holding | RW | 407117 | 7116 | I16
CM5Alt16Text |  | CONF | Text for alternative 16 for Custom Menu 5 | $ | 10 | 1078
CM5Alt16Value | 0 | CONF | Value for alternative 16 for Custom Menu 5 | I | 10 | 1081 | Holding | RW | 407118 | 7117 | I16
CM5Alt17Text |  | CONF | Text for alternative 17 for Custom Menu 5 | $ | 10 | 1083
CM5Alt17Value | 0 | CONF | Value for alternative 17 for Custom Menu 5 | I | 10 | 1086 | Holding | RW | 407119 | 7118 | I16
CM5Alt18Text |  | CONF | Text for alternative 18 for Custom Menu 5 | $ | 10 | 1088
CM5Alt18Value | 0 | CONF | Value for alternative 18 for Custom Menu 5 | I | 10 | 1091 | Holding | RW | 407120 | 7119 | I16
CM5Alt19Text |  | CONF | Text for alternative 19 for Custom Menu 5 | $ | 10 | 1093
CM5Alt19Value | 0 | CONF | Value for alternative 19 for Custom Menu 5 | I | 10 | 1096 | Holding | RW | 407121 | 7120 | I16
CM5Alt20Text |  | CONF | Text for alternative 20 for Custom Menu 5 | $ | 10 | 1098
CM5Alt20Value | 0 | CONF | Value for alternative 20 for Custom Menu 5 | I | 10 | 1101 | Holding | RW | 407122 | 7121 | I16
CM5Alt21Text |  | CONF | Text for alternative 21 for Custom Menu 5 | $ | 10 | 1103
CM5Alt21Value | 0 | CONF | Value for alternative 21 for Custom Menu 5 | I | 10 | 1106 | Holding | RW | 407123 | 7122 | I16
CM5CurrentAlt | 0 | CONF | Current alternative for Custom Menu 5 | I | 10 | 1108 | Holding | RW | 407124 | 7123 | I16 |  |  | CM5CurrentAlt | analog_value | 8048 |  | X
CM5CurrentValue | 0 | CONF | Current value for Custom Menu 5 | I | 10 | 1110 | Holding | RW | 407125 | 7124 | I16 |  |  | CM5CurrentValue | analog_value | 8049 |  | X
CM5Enabled | 0 | CONF | Enable Custom Menu 5 | L | 10 | 1112 | Coil | RW | 007010 | 7009 | U8
CM6Title |  | CONF | Title for Custom Menu 6 | $ | 10 | 1200
CM6Alt1Text |  | CONF | Text for alternative 1 for Custom Menu 6 | $ | 10 | 1203
CM6Alt1Value | 0 | CONF | Value for alternative 1 for Custom Menu 6 | I | 10 | 1206 | Holding | RW | 407126 | 7125 | I16
CM6Alt2Text |  | CONF | Text for alternative 2 for Custom Menu 6 | $ | 10 | 1208
CM6Alt2Value | 0 | CONF | Value for alternative 2 for Custom Menu 6 | I | 10 | 1211 | Holding | RW | 407127 | 7126 | I16
CM6Alt3Text |  | CONF | Text for alternative 3 for Custom Menu 6 | $ | 10 | 1213
CM6Alt3Value | 0 | CONF | Value for alternative 3 for Custom Menu 6 | I | 10 | 1216 | Holding | RW | 407128 | 7127 | I16
CM6Alt4Text |  | CONF | Text for alternative 4 for Custom Menu 6 | $ | 10 | 1218
CM6Alt4Value | 0 | CONF | Value for alternative 4 for Custom Menu 6 | I | 10 | 1221 | Holding | RW | 407129 | 7128 | I16
CM6Alt5Text |  | CONF | Text for alternative 5 for Custom Menu 6 | $ | 10 | 1223
CM6Alt5Value | 0 | CONF | Value for alternative 5 for Custom Menu 6 | I | 10 | 1226 | Holding | RW | 407130 | 7129 | I16
CM6Alt6Text |  | CONF | Text for alternative 6 for Custom Menu 6 | $ | 10 | 1228
CM6Alt6Value | 0 | CONF | Value for alternative 6 for Custom Menu 6 | I | 10 | 1231 | Holding | RW | 407131 | 7130 | I16
CM6Alt7Text |  | CONF | Text for alternative 7 for Custom Menu 6 | $ | 10 | 1233
CM6Alt7Value | 0 | CONF | Value for alternative 7 for Custom Menu 6 | I | 10 | 1236 | Holding | RW | 407132 | 7131 | I16
CM6Alt8Text |  | CONF | Text for alternative 8 for Custom Menu 6 | $ | 10 | 1238
CM6Alt8Value | 0 | CONF | Value for alternative 8 for Custom Menu 6 | I | 10 | 1241 | Holding | RW | 407133 | 7132 | I16
CM6Alt9Text |  | CONF | Text for alternative 9 for Custom Menu 6 | $ | 10 | 1243
CM6Alt9Value | 0 | CONF | Value for alternative 9 for Custom Menu 6 | I | 10 | 1246 | Holding | RW | 407134 | 7133 | I16
CM6Alt10Text |  | CONF | Text for alternative 10 for Custom Menu 6 | $ | 10 | 1248
CM6Alt10Value | 0 | CONF | Value for alternative 10 for Custom Menu 6 | I | 10 | 1251 | Holding | RW | 407135 | 7134 | I16
CM6Alt11Text |  | CONF | Text for alternative 11 for Custom Menu 6 | $ | 10 | 1253
CM6Alt11Value | 0 | CONF | Value for alternative 11 for Custom Menu 6 | I | 10 | 1256 | Holding | RW | 407136 | 7135 | I16
CM6Alt12Text |  | CONF | Text for alternative 12 for Custom Menu 6 | $ | 10 | 1258
CM6Alt12Value | 0 | CONF | Value for alternative 12 for Custom Menu 6 | I | 10 | 1261 | Holding | RW | 407137 | 7136 | I16
CM6Alt13Text |  | CONF | Text for alternative 13 for Custom Menu 6 | $ | 10 | 1263
CM6Alt13Value | 0 | CONF | Value for alternative 13 for Custom Menu 6 | I | 10 | 1266 | Holding | RW | 407138 | 7137 | I16
CM6Alt14Text |  | CONF | Text for alternative 14 for Custom Menu 6 | $ | 10 | 1268
CM6Alt14Value | 0 | CONF | Value for alternative 14 for Custom Menu 6 | I | 10 | 1271 | Holding | RW | 407139 | 7138 | I16
CM6Alt15Text |  | CONF | Text for alternative 15 for Custom Menu 6 | $ | 10 | 1273
CM6Alt15Value | 0 | CONF | Value for alternative 15 for Custom Menu 6 | I | 10 | 1276 | Holding | RW | 407140 | 7139 | I16
CM6Alt16Text |  | CONF | Text for alternative 16 for Custom Menu 6 | $ | 10 | 1278
CM6Alt16Value | 0 | CONF | Value for alternative 16 for Custom Menu 6 | I | 10 | 1281 | Holding | RW | 407141 | 7140 | I16
CM6Alt17Text |  | CONF | Text for alternative 17 for Custom Menu 6 | $ | 10 | 1283
CM6Alt17Value | 0 | CONF | Value for alternative 17 for Custom Menu 6 | I | 10 | 1286 | Holding | RW | 407142 | 7141 | I16
CM6Alt18Text |  | CONF | Text for alternative 18 for Custom Menu 6 | $ | 10 | 1288
CM6Alt18Value | 0 | CONF | Value for alternative 18 for Custom Menu 6 | I | 10 | 1291 | Holding | RW | 407143 | 7142 | I16
CM6Alt19Text |  | CONF | Text for alternative 19 for Custom Menu 6 | $ | 10 | 1293
CM6Alt19Value | 0 | CONF | Value for alternative 19 for Custom Menu 6 | I | 10 | 1296 | Holding | RW | 407144 | 7143 | I16
CM6Alt20Text |  | CONF | Text for alternative 20 for Custom Menu 6 | $ | 10 | 1298
CM6Alt20Value | 0 | CONF | Value for alternative 20 for Custom Menu 6 | I | 10 | 1301 | Holding | RW | 407145 | 7144 | I16
CM6Alt21Text |  | CONF | Text for alternative 21 for Custom Menu 6 | $ | 10 | 1303
CM6Alt21Value | 0 | CONF | Value for alternative 21 for Custom Menu 6 | I | 10 | 1306 | Holding | RW | 407146 | 7145 | I16
CM6CurrentAlt | 0 | CONF | Current alternative for Custom Menu 6 | I | 10 | 1308 | Holding | RW | 407147 | 7146 | I16 |  |  | CM6CurrentAlt | analog_value | 8050 |  | X
CM6CurrentValue | 0 | CONF | Current value for Custom Menu 6 | I | 10 | 1310 | Holding | RW | 407148 | 7147 | I16 |  |  | CM6CurrentValue | analog_value | 8051 |  | X
CM6Enabled | 0 | CONF | Enable Custom Menu 6 | L | 10 | 1312 | Coil | RW | 007011 | 7010 | U8
CM7Title |  | CONF | Title for Custom Menu 7 | $ | 10 | 1400
CM7Alt1Text |  | CONF | Text for alternative 1 for Custom Menu 7 | $ | 10 | 1403
CM7Alt1Value | 0 | CONF | Value for alternative 1 for Custom Menu 7 | I | 10 | 1406 | Holding | RW | 407149 | 7148 | I16
CM7Alt2Text |  | CONF | Text for alternative 2 for Custom Menu 7 | $ | 10 | 1408
CM7Alt2Value | 0 | CONF | Value for alternative 2 for Custom Menu 7 | I | 10 | 1411 | Holding | RW | 407150 | 7149 | I16
CM7Alt3Text |  | CONF | Text for alternative 3 for Custom Menu 7 | $ | 10 | 1413
CM7Alt3Value | 0 | CONF | Value for alternative 3 for Custom Menu 7 | I | 10 | 1416 | Holding | RW | 407151 | 7150 | I16
CM7Alt4Text |  | CONF | Text for alternative 4 for Custom Menu 7 | $ | 10 | 1418
CM7Alt4Value | 0 | CONF | Value for alternative 4 for Custom Menu 7 | I | 10 | 1421 | Holding | RW | 407152 | 7151 | I16
CM7Alt5Text |  | CONF | Text for alternative 5 for Custom Menu 7 | $ | 10 | 1423
CM7Alt5Value | 0 | CONF | Value for alternative 5 for Custom Menu 7 | I | 10 | 1426 | Holding | RW | 407153 | 7152 | I16
CM7Alt6Text |  | CONF | Text for alternative 6 for Custom Menu 7 | $ | 10 | 1428
CM7Alt6Value | 0 | CONF | Value for alternative 6 for Custom Menu 7 | I | 10 | 1431 | Holding | RW | 407154 | 7153 | I16
CM7Alt7Text |  | CONF | Text for alternative 7 for Custom Menu 7 | $ | 10 | 1433
CM7Alt7Value | 0 | CONF | Value for alternative 7 for Custom Menu 7 | I | 10 | 1436 | Holding | RW | 407155 | 7154 | I16
CM7Alt8Text |  | CONF | Text for alternative 8 for Custom Menu 7 | $ | 10 | 1438
CM7Alt8Value | 0 | CONF | Value for alternative 8 for Custom Menu 7 | I | 10 | 1441 | Holding | RW | 407156 | 7155 | I16
CM7Alt9Text |  | CONF | Text for alternative 9 for Custom Menu 7 | $ | 10 | 1443
CM7Alt9Value | 0 | CONF | Value for alternative 9 for Custom Menu 7 | I | 10 | 1446 | Holding | RW | 407157 | 7156 | I16
CM7Alt10Text |  | CONF | Text for alternative 10 for Custom Menu 7 | $ | 10 | 1448
CM7Alt10Value | 0 | CONF | Value for alternative 10 for Custom Menu 7 | I | 10 | 1451 | Holding | RW | 407158 | 7157 | I16
CM7Alt11Text |  | CONF | Text for alternative 11 for Custom Menu 7 | $ | 10 | 1453
CM7Alt11Value | 0 | CONF | Value for alternative 11 for Custom Menu 7 | I | 10 | 1456 | Holding | RW | 407159 | 7158 | I16
CM7Alt12Text |  | CONF | Text for alternative 12 for Custom Menu 7 | $ | 10 | 1458
CM7Alt12Value | 0 | CONF | Value for alternative 12 for Custom Menu 7 | I | 10 | 1461 | Holding | RW | 407160 | 7159 | I16
CM7Alt13Text |  | CONF | Text for alternative 13 for Custom Menu 7 | $ | 10 | 1463
CM7Alt13Value | 0 | CONF | Value for alternative 13 for Custom Menu 7 | I | 10 | 1466 | Holding | RW | 407161 | 7160 | I16
CM7Alt14Text |  | CONF | Text for alternative 14 for Custom Menu 7 | $ | 10 | 1468
CM7Alt14Value | 0 | CONF | Value for alternative 14 for Custom Menu 7 | I | 10 | 1471 | Holding | RW | 407162 | 7161 | I16
CM7Alt15Text |  | CONF | Text for alternative 15 for Custom Menu 7 | $ | 10 | 1473
CM7Alt15Value | 0 | CONF | Value for alternative 15 for Custom Menu 7 | I | 10 | 1476 | Holding | RW | 407163 | 7162 | I16
CM7Alt16Text |  | CONF | Text for alternative 16 for Custom Menu 7 | $ | 10 | 1478
CM7Alt16Value | 0 | CONF | Value for alternative 16 for Custom Menu 7 | I | 10 | 1481 | Holding | RW | 407164 | 7163 | I16
CM7Alt17Text |  | CONF | Text for alternative 17 for Custom Menu 7 | $ | 10 | 1483
CM7Alt17Value | 0 | CONF | Value for alternative 17 for Custom Menu 7 | I | 10 | 1486 | Holding | RW | 407165 | 7164 | I16
CM7Alt18Text |  | CONF | Text for alternative 18 for Custom Menu 7 | $ | 10 | 1488
CM7Alt18Value | 0 | CONF | Value for alternative 18 for Custom Menu 7 | I | 10 | 1491 | Holding | RW | 407166 | 7165 | I16
CM7Alt19Text |  | CONF | Text for alternative 19 for Custom Menu 7 | $ | 10 | 1493
CM7Alt19Value | 0 | CONF | Value for alternative 19 for Custom Menu 7 | I | 10 | 1496 | Holding | RW | 407167 | 7166 | I16
CM7Alt20Text |  | CONF | Text for alternative 20 for Custom Menu 7 | $ | 10 | 1498
CM7Alt20Value | 0 | CONF | Value for alternative 20 for Custom Menu 7 | I | 10 | 1501 | Holding | RW | 407168 | 7167 | I16
CM7Alt21Text |  | CONF | Text for alternative 21 for Custom Menu 7 | $ | 10 | 1503
CM7Alt21Value | 0 | CONF | Value for alternative 21 for Custom Menu 7 | I | 10 | 1506 | Holding | RW | 407169 | 7168 | I16
CM7CurrentAlt | 0 | CONF | Current alternative for Custom Menu 7 | I | 10 | 1508 | Holding | RW | 407170 | 7169 | I16 |  |  | CM7CurrentAlt | analog_value | 8052 |  | X
CM7CurrentValue | 0 | CONF | Current value for Custom Menu 7 | I | 10 | 1510 | Holding | RW | 407171 | 7170 | I16 |  |  | CM7CurrentValue | analog_value | 8053 |  | X
CM7Enabled | 0 | CONF | Enable Custom Menu 7 | L | 10 | 1512 | Coil | RW | 007012 | 7011 | U8
CM8Title |  | CONF | Title for Custom Menu 8 | $ | 10 | 1600
CM8Alt1Text |  | CONF | Text for alternative 1 for Custom Menu 8 | $ | 10 | 1603
CM8Alt1Value | 0 | CONF | Value for alternative 1 for Custom Menu 8 | I | 10 | 1606 | Holding | RW | 407172 | 7171 | I16
CM8Alt2Text |  | CONF | Text for alternative 2 for Custom Menu 8 | $ | 10 | 1608
CM8Alt2Value | 0 | CONF | Value for alternative 2 for Custom Menu 8 | I | 10 | 1611 | Holding | RW | 407173 | 7172 | I16
CM8Alt3Text |  | CONF | Text for alternative 3 for Custom Menu 8 | $ | 10 | 1613
CM8Alt3Value | 0 | CONF | Value for alternative 3 for Custom Menu 8 | I | 10 | 1616 | Holding | RW | 407174 | 7173 | I16
CM8Alt4Text |  | CONF | Text for alternative 4 for Custom Menu 8 | $ | 10 | 1618
CM8Alt4Value | 0 | CONF | Value for alternative 4 for Custom Menu 8 | I | 10 | 1621 | Holding | RW | 407175 | 7174 | I16
CM8Alt5Text |  | CONF | Text for alternative 5 for Custom Menu 8 | $ | 10 | 1623
CM8Alt5Value | 0 | CONF | Value for alternative 5 for Custom Menu 8 | I | 10 | 1626 | Holding | RW | 407176 | 7175 | I16
CM8Alt6Text |  | CONF | Text for alternative 6 for Custom Menu 8 | $ | 10 | 1628
CM8Alt6Value | 0 | CONF | Value for alternative 6 for Custom Menu 8 | I | 10 | 1631 | Holding | RW | 407177 | 7176 | I16
CM8Alt7Text |  | CONF | Text for alternative 7 for Custom Menu 8 | $ | 10 | 1633
CM8Alt7Value | 0 | CONF | Value for alternative 7 for Custom Menu 8 | I | 10 | 1636 | Holding | RW | 407178 | 7177 | I16
CM8Alt8Text |  | CONF | Text for alternative 8 for Custom Menu 8 | $ | 10 | 1638
CM8Alt8Value | 0 | CONF | Value for alternative 8 for Custom Menu 8 | I | 10 | 1641 | Holding | RW | 407179 | 7178 | I16
CM8Alt9Text |  | CONF | Text for alternative 9 for Custom Menu 8 | $ | 10 | 1643
CM8Alt9Value | 0 | CONF | Value for alternative 9 for Custom Menu 8 | I | 10 | 1646 | Holding | RW | 407180 | 7179 | I16
CM8Alt10Text |  | CONF | Text for alternative 10 for Custom Menu 8 | $ | 10 | 1648
CM8Alt10Value | 0 | CONF | Value for alternative 10 for Custom Menu 8 | I | 10 | 1651 | Holding | RW | 407181 | 7180 | I16
CM8Alt11Text |  | CONF | Text for alternative 11 for Custom Menu 8 | $ | 10 | 1653
CM8Alt11Value | 0 | CONF | Value for alternative 11 for Custom Menu 8 | I | 10 | 1656 | Holding | RW | 407182 | 7181 | I16
CM8Alt12Text |  | CONF | Text for alternative 12 for Custom Menu 8 | $ | 10 | 1658
CM8Alt12Value | 0 | CONF | Value for alternative 12 for Custom Menu 8 | I | 10 | 1661 | Holding | RW | 407183 | 7182 | I16
CM8Alt13Text |  | CONF | Text for alternative 13 for Custom Menu 8 | $ | 10 | 1663
CM8Alt13Value | 0 | CONF | Value for alternative 13 for Custom Menu 8 | I | 10 | 1666 | Holding | RW | 407184 | 7183 | I16
CM8Alt14Text |  | CONF | Text for alternative 14 for Custom Menu 8 | $ | 10 | 1668
CM8Alt14Value | 0 | CONF | Value for alternative 14 for Custom Menu 8 | I | 10 | 1671 | Holding | RW | 407185 | 7184 | I16
CM8Alt15Text |  | CONF | Text for alternative 15 for Custom Menu 8 | $ | 10 | 1673
CM8Alt15Value | 0 | CONF | Value for alternative 15 for Custom Menu 8 | I | 10 | 1676 | Holding | RW | 407186 | 7185 | I16
CM8Alt16Text |  | CONF | Text for alternative 16 for Custom Menu 8 | $ | 10 | 1678
CM8Alt16Value | 0 | CONF | Value for alternative 16 for Custom Menu 8 | I | 10 | 1681 | Holding | RW | 407187 | 7186 | I16
CM8Alt17Text |  | CONF | Text for alternative 17 for Custom Menu 8 | $ | 10 | 1683
CM8Alt17Value | 0 | CONF | Value for alternative 17 for Custom Menu 8 | I | 10 | 1686 | Holding | RW | 407188 | 7187 | I16
CM8Alt18Text |  | CONF | Text for alternative 18 for Custom Menu 8 | $ | 10 | 1688
CM8Alt18Value | 0 | CONF | Value for alternative 18 for Custom Menu 8 | I | 10 | 1691 | Holding | RW | 407189 | 7188 | I16
CM8Alt19Text |  | CONF | Text for alternative 19 for Custom Menu 8 | $ | 10 | 1693
CM8Alt19Value | 0 | CONF | Value for alternative 19 for Custom Menu 8 | I | 10 | 1696 | Holding | RW | 407190 | 7189 | I16
CM8Alt20Text |  | CONF | Text for alternative 20 for Custom Menu 8 | $ | 10 | 1698
CM8Alt20Value | 0 | CONF | Value for alternative 20 for Custom Menu 8 | I | 10 | 1701 | Holding | RW | 407191 | 7190 | I16
CM8Alt21Text |  | CONF | Text for alternative 21 for Custom Menu 8 | $ | 10 | 1703
CM8Alt21Value | 0 | CONF | Value for alternative 21 for Custom Menu 8 | I | 10 | 1706 | Holding | RW | 407192 | 7191 | I16
CM8CurrentAlt | 0 | CONF | Current alternative for Custom Menu 8 | I | 10 | 1708 | Holding | RW | 407193 | 7192 | I16 |  |  | CM8CurrentAlt | analog_value | 8054 |  | X
CM8CurrentValue | 0 | CONF | Current value for Custom Menu 8 | I | 10 | 1710 | Holding | RW | 407194 | 7193 | I16 |  |  | CM8CurrentValue | analog_value | 8055 |  | X
CM8Enabled | 0 | CONF | Enable Custom Menu 8 | L | 10 | 1712 | Coil | RW | 007013 | 7012 | U8
DisplayPosition1 | 12 | CONF | Display position 1 | X | 10 | 1800 | Holding | RW | 407195 | 7194 | U8
DisplayPosition2 | 13 | CONF | Display position 2 | X | 10 | 1801 | Holding | RW | 407196 | 7195 | U8
DisplayPosition3 | 14 | CONF | Display position 3 | X | 10 | 1802 | Holding | RW | 407197 | 7196 | U8
DisplayPosition4 | 15 | CONF | Display position 4 | X | 10 | 1803 | Holding | RW | 407198 | 7197 | U8
DisplayPosition5 | 16 | CONF | Display position 5 | X | 10 | 1804 | Holding | RW | 407199 | 7198 | U8
DisplayPosition6 | 17 | CONF | Display position 6 | X | 10 | 1805 | Holding | RW | 407200 | 7199 | U8
DisplayPosition7 | 18 | CONF | Display position 7 | X | 10 | 1806 | Holding | RW | 407201 | 7200 | U8
DisplayPosition8 | 19 | CONF | Display position 8 | X | 10 | 1807 | Holding | RW | 407202 | 7201 | U8
DisplayPosition9 | 24 | CONF | Display position 9 | X | 10 | 1808 | Holding | RW | 407203 | 7202 | U8
DisplayPosition10 | 100 | CONF | Display position 10 | X | 10 | 1809 | Holding | RW | 407204 | 7203 | U8
DisplayPosition11 | 100 | CONF | Display position 11 | X | 10 | 1810 | Holding | RW | 407205 | 7204 | U8
DisplayPosition12 | 100 | CONF | Display position 12 | X | 10 | 1811 | Holding | RW | 407206 | 7205 | U8
PLA | 254 | COM |  | X | 241 | 0
ELA | 30 | COM |  | X | 241 | 1
Ver_Minor |  | RO |  | X | 241 | 16 | Input | R | 300007 | 6 | U8
Ver_Major |  | RO |  | X | 241 | 17 | Input | R | 300006 | 5 | U8
MODEL_ALIAS |  | RO | Model number | I | 241 | 36 | Input | R | 300050 | 49 | I16
Model |  | RO | Model number | I | 241 | 36 | Input | R | 300002 | 1 | I16
Ver_Branch |  | RO |  | X | 241 | 40 | Input | R | 300008 | 7 | U8
Ver_Number |  | RO |  | X | 241 | 41 | Input | R | 300009 | 8 | U8
SerialNumberString | 0 | RO |  | $ | 241 | 60
ControllerName | RegioX | CONF |  | $ | 241 | 63 | Holding | RW | 400039 - 400070 | 38 - 69 | STRING
ControllerProject | 0 | CONF |  | $ | 241 | 66
ControllerDescription |  | CONF | Controller description | $ | 241 | 69
ControllerLocation |  | CONF | Controller location | $ | 241 | 72
UptimeMillisec | 0 | RO |  | I | 241 | 75
UptimeSec | 0 | RO |  | H | 241 | 77
GitCommit |  | RO | Internal revision number | I | 241 | 80 | Input | R | 300011 | 10 | I16
ModelName | 0 | RO |  | $ | 241 | 100
VendorName | AB Regin | RO |  | $ | 241 | 109
OSid |  | RO | Application OPERATING_SYSTEM_ID | H | 241 | 138
BACnetCommitSettings | 0 |  | Commit BACnet settings | L | 242 | 59
BACnetDeviceID | -1 | COM | BACnet device ID | H | 242 | 60
BACnetDeviceObjectName | RegioX | COM | BACnet device object name | $ | 242 | 63
BACnetSegmentationSupported | 3 | CONF | BACnet segmentation supported | X | 242 | 66
BACnetAPDUTimeout | 3000 | COM | BACnet APDU timeout | I | 242 | 67
BACnetAPDUsegmentTimeout | 2000 | COM | BACnet APDU segment timeout | I | 242 | 69
BACnetWideCharacterSetEncoding | 0 | CONF | BACnet wide character set encoding | X | 242 | 73
BACnetVendorName | AB Regin | CONF | BACnet vendor name | $ | 242 | 75
BACnetVendorIdentifier | 264 | CONF | BACnet vendor identifier | I | 242 | 78
BACnetMstpMAC_Port_1 | 0 | COM | BACnet MS/TP MAC port 1 | X | 242 | 85
BACnetMstpMaxAPDUlenAccepted_Port_1 | 480 | CONF | BACnet MS/TP max accepted APDU length port 1 | I | 242 | 86
BACnetMstpNrOfAPDUretries_Port_1 | 3 | COM | BACnet MS/TP no of APDU retries port 1 | X | 242 | 88
BACnetMstpMaxMasterAddr_Port_1 | 127 | CONF | BACnet MS/TP max master address port 1 | X | 242 | 89
BACnetMstpMaxInfoFrames_Port_1 | 1 | CONF | BACnet MS/TP max info frames port 1 | X | 242 | 90
BACnetMaxServerCOV | 100 | COM | BACnet max server COV | I | 242 | 135
BACnetPassword | gioP5TJBP8FASqREs6zX | COM | BACnet password | $ | 242 | 139
BACnetDatabaseRevisionTicker | 0 | COM | BACnet database revision ticker | I | 242 | 142
ModbusUnitID | 1 | COM | Active Modbus unit ID | X | 242 | 172 | Holding | RW | 400002 | 1 | U8
ModbusCharTimeout_Port_1 | 3 | COM |  | I | 242 | 197 | Holding | RW | 400008 | 7 | I16
ModbusAnswerDelay_Port_1 | 5 | COM |  | I | 242 | 199 | Holding | RW | 400009 | 8 | I16
Mode_Port_1 | 2 | RO | Active RS485 port mode/protocol | X | 248 | 0
Format_Port_1 | 112 | RO | Active RS485 port format | X | 248 | 35
TimeOut_Port_1 | 0 | RO |  | X | 248 | 38
Baud_Port_1 | 0 | RO | Active RS485 port baud rate | X | 248 | 41
Note on C3: RO = Read only variable COM = Communication settings [Non volatile] CONF = Configuration settings [Non volatile]
Note on L3: LOGIC: Used for True/False values, only allowed for "Discrete inputs" and "Coils" U8: One 8 bit unsigned integer variable to/from LSB of one register I16: One 16 bit integer variable to/from one register I16SO: Floating point variable converted to 16 bit integer to/from one register. Scale and Offset used REGx2IEEE: First register: MSW of floating point variable to/from one 16-bit register (IEEE) Second register: LSW of floating point variable to/from one 16-bit register (IEEE) REGx2I32: First register: MSW of 32 bit integer variable to/from one 16-bit register Second register: LSW of 32 bit integer variable to/from one 16-bit register REGx2I32SO: First register: MSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O Second register: LSW of 32 bit integer converted from floating point variable. Scale & Offset used. R/O
Note on D6: 0 = Device running normally 23040 = Do nothing 23041 = Cools reset 23042 = Upgrade 23043 = Colds 23044 = Power up 23045 = Warm reset 23046 = Save config as user default 23047 = Restore config from user default 23048 = Switch to Bluetooth Direct Test Mode
Note on D9: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on P9: 1 = Inactive 3 = EXOline slave 14 = BACnet 16 = Modbus slave 22 = EXOline/Modbus autodetect
Note on D10: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s
Note on P10: 1 = 9600 bits/s 3 = 2400 bits/s 4 = 1200 bits/s 16 = 19200 bits/s 18 = 38400 bits/s 19 = 57600 bits/s 21 = 115200 bits/s 22 = 230400 bits/s 23 = 460800 bits/s 26 = 921k6 bits/s 27 = 1000000 bits/s 28 = 250000 bits/s
Note on D11: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on P11: 17 = 8 bit, no parity, 1 stop bit 25 = 8 bit, no parity, 2 stop bits 49 = 8 bit, even parity, 1 stop bit 57 = 8 bit, even parity, 2 stop bits 113 = 8 bit, odd parity, 1 stop bit 121 = 8 bit, odd parity, 2 stop bits
Note on D17: 0 = Disabled 1 = Set outputs to default values 2 = Set controller state to a default value 3 = Set outputs to default values, start device in offline mode
Note on P17: 1 = Disabled 2 = Set outputs to default values 3 = Set controller state to a default value 4 = Set outputs to default values, start device in offline mode
Note on D21: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on D23: 0 = LED off 224 = Red 28 = Green 3 = Blue 252 = Yellow 31 = Cyan 227 = Magenta 255 = White
Note on D25: 0 = No faults 1 = Internal Error 2 = Calibration Lost during startup 4 = Calibration memory failed
Note on D34: 0 = Always off 1 = Always on 2 = On at startup 3 = On with button press
Note on D44: 0 = 0x00 -20.4 dBm 6 = 0x06 -19.4 dBm 7 = 0x07 -18.3 dBm 8 = 0x08 -17.3 dBm 9 = 0x09 -16.4 dBm 10 = 0x0A -15.4 dBm 11 = 0x0B -14.3 dBm 12 = 0x0C -13.3 dBm 13 = 0x0D -12.3 dBm 14 = 0x0E -11.4 dBm 15 = 0x0F -10.4 dBm 16 = 0x10 -9.5 dBm 17 = 0x11 -8.4 dBm 18 = 0x12 -7.5 dBm 19 = 0x13 -6.5 dBm 20 = 0x14 -5.4 dBm 21 = 0x15 -4.5 dBm 22 = 0x16 -3.5 dBm 23 = 0x17 -2.4 dBm 24 = 0x18 -1.5 dBm 25 = 0x19 -0.3 dBm 26 = 0x1A +0.9 dBm 27 = 0x1B +2.3 dBm 28 = 0x1C +2.8 dBm 29 = 0x1D +3.9 dBm 30 = 0x1E +4.8 dBm 31 = 0x1F +5.6 dBm 32 = 0x20 +6.9 dBm 33 = 0x21 +7.5 dBm 34 = 0x22 +8.5 dBm 35 = 0x23 +10 dBm
Note on D54: 0 = Off 1 = Green 2 = Yellow 3 = Red
Note on P54: 1 = Off 2 = Green 3 = Yellow 4 = Red
Note on D65: 0 = Fan off 1 = Fan at low speed 2 = Fan at medium speed 3 = Fan at high speed 4 = Fan in Auto mode
Note on P65: 1 = Fan off 2 = Fan at low speed 3 = Fan at medium speed 4 = Fan at high speed 5 = Fan in Auto mode
Note on D74: 0 = Actual temperature 1 = Heat setpoint 2 = Cool setpoint 3 = Average value of heating and cooling setpoint 4 = Setpoint offset 5 = Deprecated, do not use 6 = Heat setpoint + offset 7 = Cool setpoint + offset 8 = Average setpoint + offset 9 = Calculated air flow 10 = Active setpoint + offset
Note on P74: 1 = Actual temperature 2 = Heat setpoint 3 = Cool setpoint 4 = Average value of heating and cooling setpoint 5 = Setpoint offset 6 = Deprecated, do not use 7 = Heat setpoint + offset 8 = Cool setpoint + offset 9 = Average setpoint + offset 10 = Calculated air flow 11 = Active setpoint + offset
Note on D75: 0 = Setpoint offset 1 = Active setpoint + offset 2 = Heat setpoint + offset 3 = Cool setpoint + offset 4 = Heat occupied setpoint + offset 5 = Cool occupied setpoint + offset 6 = Average setpoint + offset
Note on P75: 1 = Setpoint offset 2 = Active setpoint + offset 3 = Heat setpoint + offset 4 = Cool setpoint + offset 5 = Heat occupied setpoint + offset 6 = Cool occupied setpoint + offset 7 = Average setpoint + offset
Note on D82: 0 = Always off 1 = Show only when the value is displayed 2 = Always on
Note on D83: 0 = Controller mode Off 1 = Controller mode Heating 2 = Controller mode Cooling
Note on D92: 0 = Do not display any boot screen 1 = Display device type 2 = Display device type and model 3 = Display device type, model and version 4 = Display device type, model, version and addresses
Note on D93: 0 = Adapt font to fit on screen, use as large as possible, if it does not fit, use scrolling and smalest font 1 = 5 pixels high font 2 = 7 pixels high font 3 = 10 pixels high font
Note on P93: 1 = Adapt font to fit on screen, use as large as possible, if it does not fit, use scrolling and smalest font 2 = 5 pixels high font 3 = 7 pixels high font 4 = 10 pixels high font
Note on D94: 0 = Show only one row of text 1 = Show two rows of text
Note on P94: 1 = Show only one row of text 2 = Show two rows of text
Note on D95: 0 = Wrap text at the end 1 = Bounce between start and end position 2 = Wrap text at the end, sync row 1 and 2 3 = Bounce between start and end position, sync row 1 and 2
Note on P95: 1 = Wrap text at the end 2 = Bounce between start and end position 3 = Wrap text at the end, sync row 1 and 2 4 = Bounce between start and end position, sync row 1 and 2
Note on D97: 0 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 1 = Force display until remaining time is 0 2 = Show as a menu item as long as text is not empty
Note on P97: 1 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 2 = Force display until remaining time is 0 3 = Show as a menu item as long as text is not empty
Note on D101: 0 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 1 = Force display until remaining time is 0 2 = Show as a menu item as long as text is not empty
Note on P101: 1 = Show when remaing time is > 0, show as meny item if a buttom has been pressed until remaingtime is 0 2 = Force display until remaining time is 0 3 = Show as a menu item as long as text is not empty
Note on D114: 0 = Disabled 1 = Enabled 2 = Read only
Note on D115: 0 = Disabled 1 = Enabled 2 = Read only
Note on D116: 0 = Disabled 1 = Enabled 2 = Read only
Note on D117: 0 = Disabled 1 = Enabled 2 = Read only
Note on D118: 0 = Disabled 1 = Enabled 2 = Read only
Note on D119: 0 = Disabled 1 = Enabled 2 = Read only
Note on D120: 0 = Disabled 1 = Enabled 2 = Read only
Note on D139: 0 = Disabled 1 = Enabled 2 = Read only
Note on D559: 0 = Inactive 2 = EXOline slave 13 = BACnet 15 = Modbus slave 21 = EXOline/Modbus autodetect
Note on D560: 16 = 8 bit, no parity, 1 stop bit 24 = 8 bit, no parity, 2 stop bits 48 = 8 bit, even parity, 1 stop bit 56 = 8 bit, even parity, 2 stop bits 112 = 8 bit, odd parity, 1 stop bit 120 = 8 bit, odd parity, 2 stop bits
Note on D562: 0 = 9600 bits/s 2 = 2400 bits/s 3 = 1200 bits/s 15 = 19200 bits/s 17 = 38400 bits/s 18 = 57600 bits/s 20 = 115200 bits/s 21 = 230400 bits/s 22 = 460800 bits/s 25 = 921k6 bits/s 26 = 1000000 bits/s 27 = 250000 bits/s